## FrontPage
Cost-of-Service tool - Version 2.0
Update
2025
IRENA’s spreadsheet-based Electricity Storage Cost-of-Service Tool 2.0 offers an updated quick and accessible way to estimate the annual cost of storage services for different technologies and applications. While not a detailed investment model, it allows users to identify potentially cost-effective options for further assessment of performance, suitability, and economics.
The tool allows users to analyze a wide range of energy storage technologies (including mechanical, electrochemical, and chemical) across multiple applications (see the Applications tab). Each configuration can be defined through user-selected parameters such as technology type, application, operational conditions, system size, and location, considering the effect of cycling.
Based on these user-defined scenarios, the tool calculates investment and operating costs, as well as the resulting levelized cost of storage (LCOS), enabling comparative assessments under different design and market assumptions.
Levelized Cost of Storage 2025-2030
Energy Storage Applications
Energy Storage Technologies
System configuration

## Instructions
Instructions
The purpose of this tool is to assist you in determining the cost-of-service of different storage technologies.
This sheet provides step-by-step instruction on how to utilise it.
| Contact information: | costs@irena.org
Disclaimer
This tool is based on data which were compiled from over 150 data sources, supplemented by expert interviews and analysis by IRENA of the latest battery developments.
As a result, this data is a blend of different analytical approaches, including data from: installed projects, regulatory databases, installer surveys, individual projects, bottom-up engineering analyses and learning curve studies.
Given the rapidly changing market place for electricity storage and the difficulty in always obtaining up-to-date data for each technology, the results should be treated with caution.
The methodology of the calculations is explained in Tab "Methodology"
Step 1
Select the 'Cost of Service' sheet.
Select the storage technology option that you wish to evaluate:
Step 2
Select the Power conversion unit to evaluate:
Note: After you have changed the energy storage unit choice the first time, you may need to adjust the power conversion unit choice again, from those available in the dropdown.
Step 3
Select the grid connection to evaluate:
Note: You can also choose no grid connection to compare the technologies independent of the desired location
Step 4
Select the storage size to evaluate:
Note: there is a suitability check if the storage size fits to your storage type. If not you can adjust your storage sizing
Step 5
Select the application type to evaluate:
Note: The tool contains 18 predefined storage applications, which can be chosen from this dropdown menu. More information on each application is available in "Application" sheet. Parameters can be modified and new applications can be added by the user.
To create new ones, also "Applications: Modifying parameters or creating new applications" section at the end of this sheet.
Step 6
If available, you can add additional information on local conditions:
Note: The tool assumes the same value you input would apply for all cases in each period.
Step 7
The cyclic aging of the storage type is considered
Note: Standard classifications for storages and the fatigue exponents are used in the tool. Id you want to igore it or if you have own fatigue experiences you can put in own values.
Results: Key results
The tool displays results for major calculation steps and also displays a summary of the results as shown below:
Visualisation: Technology Development
Select the 'Visualization' sheet.
The tool contains charts to visualise the key results and provides a summarized table of cost-of-services estimates for the selected technology and application combination evaluated.
Visualization: Technology Comparison
Select the 'Visualization' sheet.
The tool provides a section where you can store some of the runs of estimates that you have done and in this way compare different technology options. It also charts these so you can visualise them automatically.
Applications: Modifying parameters or creating new applications
In the 'Applications' sheet, the tool provides a section where you can modify the 18 predefined storage applications altering their key parameters. You also have the option to define your own applications defining them by these parameters.
If you add additional applications to the 'Applications' sheet, they will appear as an option in the 'Cost-of-Service' sheet (see Step 3 of these instructions).

## Cost-of-Service
Energy Storage Unit
|  | 2016 |  |  | 2025 |  |  | 2030
Choose ---> | Li-Ion (LFP) | best | worst | reference | best | worst | reference | best | worst | reference | unit
| Energy density | 620 | 200 | 350 | 620 | 200 | 350 | 620 | 200 | 350 | Wh/l
| Power density | 10000 | 100 | 3500 | 10000 | 100 | 3500 | 10000 | 100 | 3500 | W/l
| Cycle life | 10000 | 1000 | 2500 | 20000 | 2000 | 5000 | 30000 | 3000 | 7500 | equivalent full-cycles
| Calendar life | 20 | 5 | 12 | 28.3333 | 7.0833 | 17 | 33.3333 | 8.3333 | 20 | a
| Depth of discharge | 100 | 84 | 90 | 100 | 84 | 90 | 100 | 84 | 90 | %
| Round-trip efficiency | 90 | 81 | 86 | 96.2791 | 86.6512 | 92 | 98.3721 | 88.5349 | 94 | %
| Self-discharge | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.1 | % per day
| Power dynamic | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | s to rated power
| Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
| Energy installation cost | 199.5 | 840 | 577.5 | 67.3636 | 283.6364 | 195 | 36.9636 | 155.6364 | 107 | USD / kWh
| Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
| E/P ratio limitation | 0.33333 | 1 | 0.66667 | 0.33333 | 1 | 0.66667 | 0.33333 | 1 | 0.66667 | h
Power Conversion Unit
|  | 2016 |  |  | 2025 |  |  | 2030
Choose ---> | Inverter large | best | worst | reference | best | worst | reference | best | worst | reference | unit
| Energy density | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | Wh/l
| Power density | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0.15 | W/l
| Cycle life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
| Calendar life | 25 | 19 | 20 | 33.75 | 25.65 | 27 | 37.5 | 28.5 | 30 | a
| Depth of discharge | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 90 | %
| Round-trip efficiency | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | %
| Self-discharge | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0.01 | % per day
| Power dynamic | - | - | 0.02 | 0 | 0 | 30 | 0 | 0 | 30 | s to rated power
| Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | a
| Energy installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
| Power installation cost | 73.5 | 189 | 105 | 49 | 126 | 70 | 38.5 | 99 | 55 | USD / kW
Grid Connection
|  | 2016 |  |  | 2025 |  |  | 2030
Choose ---> | Low Voltage Grid | best | worst | reference | best | worst | reference | best | worst | reference | unit
| Connection Costs | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | USD / kW
| Equipment Costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
| Lifetime | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | a
| Round-trip efficiency | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Storage Size
|  | 2016 |  |  | 2025 |  |  | 2030
Choose ---> | typical PHS | best | worst | reference | best | worst | reference | best | worst | reference | unit
| Power | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | kW
| Energy | 8500000 | 8500000 | 8500000 | 8500000 | 8500000 | 8500000 | 8500000 | 8500000 | 8500000 | kWh
| E/P Ratio | 8.0189 | 8.0189 | 8.0189 | 8.0189 | 8.0189 | 8.0189 | 8.0189 | 8.0189 | 8.0189 | h
| Suitability of Storage | OK | OK | OK | OK | OK | OK | OK | OK | OK | Suitability Check
Application
|  | 2016 |  |  | 2025 |  |  | 2030
Choose ---> | Increase Power Quality | best | worst | reference | best | worst | reference | best | worst | reference | unit
| required Power (bid size) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | kW
| required energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | kWh
| E/P Ratio | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | h
| Depth of discharge | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | %
| Cycles per day | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | -
| Type | Power | Power | Power | Power | Power | Power | Power | Power | Power
| Electricity price [UScents / kWh] | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | US
Country-specific data
|  | 2016 |  |  | 2025 |  |  | 2030
Choose --> | Put additional data here if available | best | worst | reference | best | worst | reference | best | worst | reference | unit
| Maintenance storage system | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | % of invest per year
| Maintenance power conversion unit | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | % of invest per year
| Maintenance grid connection | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | % of invest per year
| Interest rate | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | %
| Other fixed costs (upfront) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD
| Other fixed costs (yearly) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD per year
Cyclic Aging Coefficient
|  | 2016 |  |  | 2025 |  |  | 2030
Choose --> | Put additional data here if available | best | worst | reference | best | worst | reference | best | worst | reference | unit
| Storage Type | Ion-Battery | Ion-Battery | Ion-Battery | Ion-Battery | Ion-Battery | Ion-Battery | Ion-Battery | Ion-Battery | Ion-Battery | Type
| Fatigue Exponent | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | FadeFactor
| Own Fatigue Exponent (use 1 for non use) | [9 empty] | FadeFactor
| equivalent full cycles | 50000 | 5000 | 12500 | 100000 | 10000 | 25000 | 150000 | 15000 | 37500 | equivalent full-cycles
Calculations
|  | 2016 |  |  | 2025 |  |  | 2030
|  | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy Storage Unit
| Installed Storage Power | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | kW
| Usable Storage Power (Application) | 1059996 | 1059996 | 1059996 | 1059996 | 1059996 | 1059996 | 1059996 | 1059996 | 1059996 | kW
| Installed Storage Capacity | 8500000 | 8500000 | 8500000 | 8500000 | 8500000 | 8500000 | 8500000 | 8500000 | 8500000 | kWh
| Usable Storage Capacity (technical) | 8500000 | 7140000 | 7650000 | 8500000 | 7140000 | 7650000 | 8500000 | 7140000 | 7650000 | kWh
| Usable Storage Capacity (Application) | 8500000 | 7140000 | 7650000 | 8500000 | 7140000 | 7650000 | 8500000 | 7140000 | 7650000 | kWh
| Lifetime in application | 20 | 5 | 12 | 28.3333 | 7.0833 | 17 | 33.3333 | 8.3333 | 20 | a
| Total Storage Invest | 1695750000 | 5997600000 | 4417875000 | 572590909.0909 | 2025163636.3636 | 1491750000 | 314190909.0909 | 1111243636.3636 | 818550000 | USD
| Annuities Energy Storage Unit | 110661200.1528 | 1271459589.7399 | 430901879.4746 | 29402596.2275 | 312242364.8476 | 110002122.0355 | 14602879.9062 | 148244560.7928 | 53416910.1489 | USD
Power Conversion Unit
| Installed Conversion Power | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | kW
| Total Conversion Invest | 77910000 | 200340000 | 111300000 | 51940000 | 133560000 | 74200000 | 40810000 | 104940000 | 58300000 | USD
| Annuities Power Conversion Unit | 4343888.7696 | 13579138.6717 | 7263211.8986 | 2396576.9737 | 7319323.0362 | 3930742.1418 | 1774272.0989 | 5368548.0194 | 2887789.144 | USD
Grid Connection
| Installed Grid Capacity | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | 1060000 | kW
| Total Grid Connection Invest | 106000000 | 106000000 | 106000000 | 106000000 | 106000000 | 106000000 | 106000000 | 106000000 | 106000000 | USD
| Annuities Grid Connection | 3999749.9134 | 3999749.9134 | 3999749.9134 | 3999749.9134 | 3999749.9134 | 3999749.9134 | 3999749.9134 | 3999749.9134 | 3999749.9134 | USD
Total Invest
| Energy Storage + Power Conversion + Grid Connection | 1879660000 | 6303940000 | 4635175000 | 730530909.0909 | 2264723636.3636 | 1671950000 | 461000909.0909 | 1322183636.3636 | 982850000 | USD
| Total Invest per usable kWh storage | 221.1365 | 741.64 | 545.3147 | 85.9448 | 266.4381 | 196.7 | 54.2354 | 155.551 | 115.6294 | USD
Energy losses
| Energy throughput per year (only one direction) | 38689854 | 38689854 | 38689854 | 38689854 | 38689854 | 38689854 | 38689854 | 38689854 | 38689854 | kWh
| Total Round-Trip-Efficiency | 88.2 | 79.38 | 84.28 | 94.3535 | 84.9181 | 90.16 | 96.4047 | 86.7642 | 92.12 | %
| Efficiency losses per year [kWh] | 4565402.772 | 7977847.8948 | 6082045.0488 | 2184627.1049 | 5835149.7944 | 3807081.6336 | 1391035.2159 | 5120917.0943 | 3048760.4952 | kWh
| Efficiency losses per year [USD] | 1323966.8039 | 2313575.8895 | 1763793.0642 | 633541.8604 | 1692193.4404 | 1104053.6737 | 403400.2126 | 1485065.9574 | 884140.5436 | USD
| Self-discharge losses per year [kWh] | 2792250 | 9381960 | 2792250 | 2792250 | 9381960 | 2792250 | 2792250 | 9381960 | 2792250 | kWh
| Self-discharge losses per year [USD] | 809752.5 | 2720768.4 | 809752.5 | 809752.5 | 2720768.4 | 809752.5 | 809752.5 | 2720768.4 | 809752.5 | USD
Annuities
| Annuities Invest | 119004838.8358 | 1289038478.325 | 442164841.2866 | 35798923.1146 | 323561437.7971 | 117932614.0908 | 20376901.9185 | 157612858.7256 | 60304449.2064 | USD
| Capital | 90023900 | 1212184210.5263 | 375841250 | 23868053.8721 | 293232472.0893 | 92618148.1481 | 12633993.9394 | 139151341.6268 | 44990833.3333 | USD
| Financing | 28980938.8358 | 76854267.7987 | 66323591.2866 | 11930869.2425 | 30328965.7078 | 25314465.9426 | 7742907.9791 | 18461517.0988 | 15313615.8731 | USD
| Maintenance | 27664900 | 94029100 | 68997625 | 10427963.6364 | 33440854.5455 | 24549250 | 6385013.6364 | 19302754.5455 | 14212750 | USD
| Efficiency losses | 1323966.8039 | 2313575.8895 | 1763793.0642 | 633541.8604 | 1692193.4404 | 1104053.6737 | 403400.2126 | 1485065.9574 | 884140.5436 | USD
| Self-discharge | 809752.5 | 2720768.4 | 809752.5 | 809752.5 | 2720768.4 | 809752.5 | 809752.5 | 2720768.4 | 809752.5 | USD
| Sum | 148803458.1397 | 1388101922.6145 | 513736011.8508 | 47670181.1114 | 361415254.183 | 144395670.2645 | 27975068.2675 | 181121447.6284 | 76211092.25 | USD
Key Results
|  | 2016 |  |  | 2025 |  |  | 2030
|  | best | worst | reference | best | worst | reference | best | worst | reference | unit
Levelised Cost-of-Service
Results --> | Cost of 1 kW Storage System per year [USD] | 140.3806 | 1309.5301 | 484.6566 | 44.9719 | 340.9578 | 136.2223 | 26.3916 | 170.8693 | 71.8973 | USD
Results --> | Cost of 1 kWh stored electricity [USDct] | 384.6059 | 3587.7673 | 1327.8314 | 123.2111 | 934.1344 | 373.2133 | 72.306 | 468.1368 | 196.9795 | USDct
[6 empty] | Suitable: | OK | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[6 empty] | Validity check: | OK | 1 | 1 | 1

## Visualization
Technology Comparison
Increase Power Quality
Choose ---> | Electricity | 2016 | 2025 | 2030 | Unit
| Pumped Hydro | 2.9854 | 3.6075 | 3.6075 | USD cents per kWh
| CAES | 7.059 | 6.0296 | 6.0159 | USD cents per kWh
| Vanadium Flow | 27.9325 | 21.6146 | 18.3896 | USD cents per kWh
| Li-Ion (LFP) | 22.7909 | 5.2315 | 2.6345 | USD cents per kWh
| SIB (Layered oxide) | #N/A | 15.6936 | 13.3648 | USD cents per kWh
Copy results into table
| Li-Ion (LFP) | 1327.8314 | 373.2133 | 196.9795 | USD cents per kWh
|  |  |  | Validity check: | OK
Technology Development
Increase Power Quality
| Li-Ion (LFP) | 2016 | 2025 | 2030 | Unit
| Best | 384.6059 | 123.2111 | 72.306 | USD cents per kWh
| Worst | 3587.7673 | 934.1344 | 468.1368 | USD cents per kWh
| Reference | 1327.8314 | 373.2133 | 196.9795 | USD cents per kWh

## Grid Connection (hidden)
| [$/kVA] | [$/kVA] | [a] | [%]
| Connection Costs | Equipment Costs | Lifetime | Round-trip efficiency | Comment
Low Voltage Grid | 100 | 0 | 50 | 100 | German grid, without "Baukostenzuschuss"
Medium Voltage no transformer | 30 | 0 | 50 | 100 | German grid, without "Baukostenzuschuss"
Medium Voltage incl. transformer | 30 | 35 | 50 | 96 | German grid, without "Baukostenzuschuss"
High Voltage incl. transformer | 15 | 15 | 50 | 96 | German grid, without "Baukostenzuschuss"
High Voltage incl. Transformer & substation | 15 | 61 | 50 | 95 | German grid, without "Baukostenzuschuss"
no grid connection necessary | 0 | 0 | 0 | 100
Put more Grid Connection Options here

## Storage Size (hidden)
| [kW] | [kWh] | [kWh/kW]
| Power | Energy | E/P Ratio | Comment
typical 2h battery storage | 1000 | 2000 | 2 | Use green fields to put in data of your own Storage
typical battery storage for FCR | 5400 | 5600 | 1.037 | 5MW design comparable to WEMAG or M5BAT
typical PHS | 1060000 | 8500000 | 8.0189 | Largest PHS in Germany: Goldisthal, operational since 1991
typical CAES | 300000 | 1500000 | 5 | Energy Storage No. 1, Largest CAES, Hubei Province, China
typical self-consumtion | 5 | 10 | 2
typical community storage | 224 | 191.36 | 0.85429 | EnergyNeighbor research project
typical storage for I&C | 100 | 250 | 2.5
typical storage for Village electrification | 50 | 125 | 2.5 | Small village in Columbia
typical storage for Island grid | 800 | 2800 | 3.5 | Greek island Tilos: 2x 400 kWh ZEBRA battery used for RE integration
Put more Storages here

## Applications
| [kW] | [kWh] | [kWh/kW] | [%] | [N/day] |  | [UScents/kWH]
| required power (bid size) | required energy | E/P Ratio | Depth of discharge | Cycles per day | Type | Electricity price | Level | Comment
Reactive power provision | 1 | 1 | 1 | 5 | 0.1 | Power | 10 | Utility-scale grid support | possible via STATCOM or BESS no market available. Theoretical possible with any storage
Synthetic Inertia | 1000 | 50 | 0.05 | 1 | 1 | Power | 10 | Utility-scale grid support | !!! Estimates !!! - There is no market available today. Bid sizes are likley --> oriented on other markets
Fast Frequency Response (FFR) | 1000 | 50 | 0.05 | 1 | 0.5 | Power | 10 | Utility-scale grid support | !!! Estimates !!! --> oriented on other markets
Enhanced Frequency Respose (EFR) | 1000 | 500 | 0.5 | 5 | 0.5 | Power | 10 | Utility-scale grid support | !!! Estimates !!! --> oriented on other markets
Frequency Containment Reserve (FCR) | 1000 | 810 | 0.81 | 10 | 0.8 | Power | 10 | Utility-scale grid support | TSO Central Europe (GER), M5BAT Research
automatic Frequency Restoration Reserve (aFRR) | 1000 | 250 | 0.25 | 20 | 0.5 | Energy | 10 | Utility-scale grid support | TSO Central Europe (GER), M5BAT Research
Spot Market Trading (arbitrage) | 400 | 100 | 0.25 | 80 | 2 | Energy | 10 | Utility-scale grid support | EPEX SPOT
FCR + arbitrage | 1400 | 910 | 0.65 | 50 | 1.5 | Power | 10 | Utility-scale grid support | ISEA RWTH; !!! Estimates !!! --> oriented on other markets and expertise
aFRR + arbitrage | 1400 | 350 | 0.25 | 50 | 1.2 | Energy | 10 | Utility-scale grid support | ISEA RWTH; !!! Estimates !!! --> oriented on other markets and expertise
FCR + aFRR + arbitrage | 2400 | 1160 | 0.48333 | 70 | 2 | Energy | 10 | Utility-scale grid support | ISEA RWTH; !!! Estimates !!! --> oriented on other markets and expertise
Self-consumption (small residential) | 2.5 | 5 | 2 | 80 | 0.60274 | Energy | 29 | Behind-the-meter systems | Typical PV Battery System in Germany (see Appendix of report)
Community storage | 224 |  | 0.85429 | 60 | 1 | Energy | 29 | Behind-the-meter systems | EnergyNeighbor research project
Increase Power Quality | 12 |  | 2 | 20 | 0.1 | Power | 29 | Behind-the-meter systems | ISEA RWTH
Peak shaving | 200 |  | 0.3 | 25 | 0.054795 |  | 18 | Behind-the-meter systems | ISEA RWTH
Time-of-use | 5 |  | 4 | 80 | 1 |  | 20 | Behind-the-meter systems
Nano Offgrid | 0.2 |  | 2 | 2 | 0.85 |  | 100 | Off-grid aplications | Small hut with 200W PV
Village electrification | 50 |  | 2.5 | 2.5 | 0.9 |  | 100 | Off-grid aplications | Small village in Columbia
Island grid | 800 |  | 3.5 | 3.5 | 1 |  | 100 | Off-grid aplications | Greek island Tilos: 2x 400 kWh ZEBRA battery used for RE integration
Put more applications here
Insert more applications as needed here in the blank rows of the table. You can also modify parameters of predefined ones.
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Quellen mit Grid Services https://doi.org/10.33423/jsis.v15i8.3923 https://doi.org/10.3390/en13040917

## Wohler-Curve (hidden)
The cyclical capabilities of the storage system are mapped by the Wöhler curve, so that a higher cyclical stability is assumed for smaller DODs. The decrease in capacity due to aging is not taken into account, as the entire capacity is not utilized with small DODs.
| Ermüdungsexponent b | 2
| nom Cycles N_nom | 10000
| DOD in % | 5 | 200000
|  | 10 | 100000
|  | 15 | 66666.6667
|  | 20 | 50000
|  | 25 | 40000
|  | 30 | 33333.3333
|  | 35 | 28571.4286
|  | 40 | 25000
|  | 45 | 22222.2222
|  | 50 | 20000
|  | 55 | 18181.8182
|  | 60 | 16666.6667
|  | 65 | 15384.6154
|  | 70 | 14285.7143
|  | 75 | 13333.3333
|  | 80 | 12500
|  | 85 | 11764.7059
|  | 90 | 11111.1111
|  | 95 | 10526.3158
|  | 100 | 10000
𝐸𝐹𝐶=𝑁_𝑛𝑜𝑚•((𝐷𝑂𝐷_𝑛𝑜𝑚)/𝐷𝑂𝐷)^𝑏•𝐷𝑂𝐷/(𝐷𝑂𝐷_𝑛𝑜𝑚 )
Note on C8: Author: 2-3 for Li-Batterien 4-7 für mechanische Speicher

## Methodology
Methodology

## List of PCUs (hidden)
Inverter small
Inverter large
No Inverter
Generator PHS
Generator CAES
Generator Flywheel
Modular Multilevel Converter
<-- If new PCU technologies are added, reference them here

## List of Storage Technologies (hidden)
Pumped Hydro
CAES
Flywheel
Flooded LA
VRLA
Li-Ion (LFP)
Li-Ion (NMC)
Li-Ion (Titanate)
NaNiCl
NaS
Vanadium Flow
ZnBr Flow
ZnBr (Zinc ion)
SIB (Layered oxide) | <-- If new storage technologies are added, reference them here

## Financials (hidden)
US Dollar (USD) to Euro (EUR) conversion |  | Euro (EUR) to US Dollar (USD) conversion
Year | Rate | Year | Rate
2010 | 0.754 | 2010 | 1.3263
2011 | 0.718 | 2011 | 1.3928
2012 | 0.778 | 2012 | 1.2853
2013 | 0.753 | 2013 | 1.328
2014 | 0.753 | 2014 | 1.328
2015 | 0.901 | 2015 | 1.1099
2016 | 0.903 | 2016 | 1.1074
2017 | 0.885 | 2017 | 1.1299
2018 | 0.847 | 2018 | 1.1806
2019 | 0.893 | 2019 | 1.1198
2020 | 0.876 | 2020 | 1.1416
2021 | 0.846 | 2021 | 1.182
2022 | 0.95 | 2022 | 1.0526
2023 | 0.925 | 2023 | 1.0811
2024 | 0.924 | 2024 | 1.0823
2025* | 0.924 | 2025* | 1.0823
Currency exchange rates for the Euro area as published in the European Central Bank (ECB) data portal: https://data.ecb.europa.eu/data/datasets/EXR/EXR.A.USD.EUR.SP00.A
*Same as 2024

## Overview 2016 (in) (hidden)
Mechanical
| Pumped Hydro |  |  | CAES |  |  | Flywheel
| best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 2 | 0.2 | 1 | 6 | 2 | 3 | 200 | 20 | 80 | Wh/l
Power density | 0.2 | 0.1 | 0.15 | 0.6 | 0.2 | 0.4 | 10000 | 5000 | 7500 | W/l
Cycle life | 100000 | 12000 | 50000 | 100000 | 10000 | 50000 | 1000000 | 100000 | 200000 | equivalent full-cycles
Calendar life | 100 | 30 | 60 | 100 | 20 | 50 | 25 | 15 | 20 | a
Depth of discharge | 100 | 80 | 90 | 50 | 35 | 40 | 90 | 75 | 85 | %
Round-trip efficiency | 92 | 70 | 80 | 80 | 40 | 60 | 99 | 70 | 84 | %
Self-discharge | 0 | 0.02 | 0.01 | 0 | 1 | 0.5 | 20 | 100 | 60 | % per day
Power dynamic | 15 | 500 | 30 | sec | 900 | 480 | < 0,004 | sec | 0.05 | s to rated power
Planning & Construction Time | 5 | 25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 5.25 | 100 | 21 | 2 | 84 | 52.5 | 1500 | 6000 | 3000 | USD / kWh
Power installation cost | 525 | 2000 | 840 | 400 | 1050 | 735 | 315 | 1050 | 300 | USD / kW
| Lead-Acid | [5 empty] | Li-Ion
| Flooded LA |  |  | VRLA |  |  | NMC/LMO
| best | worst | ref | best | worst | ref | best | worst | ref | unit
Energy density | 100 | 50 | 80 | 100 | 50 | 80 | 735 | 200 | 468 | Wh/l
Power density | 700 | 10 | 350 | 700 | 10 | 350 | 10000 | 100 | 3500 | W/l
Cycle life | 2500 | 250 | 1500 | 2500 | 250 | 1500 | 4000 | 500 | 2000 | equivalent full-cycles
Calendar life | 15 | 3 | 9 | 15 | 3 | 9 | 20 | 5 | 12 | a
Depth of discharge | 50 | 60 | 50 | 50 | 60 | 50 | 100 | 84 | 90 | %
Round-trip efficiency | 92 | 75 | 82 | 92 | 75 | 82 | 98 | 81 | 92 | %
Self-discharge | 0.09 | 0.4 | 0.25 | 0.09 | 0.4 | 0.25 | 0.09 | 0.36 | 0.1 | % per day
Power dynamic | 0.003 | 0.01 | 0.006 | 0.003 | 0.01 | 0.006 | 0.003 | 1 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 105 | 472.5 | 194.25 | 105 | 472.5 | 210 | 199.5 | 840 | 420 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
Li-Ion
| NCA |  |  | LiFePo4 |  |  | Titanate
| best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 620 | 200 | 350 | 620 | 200 | 350 | 620 | 200 | 350 | Wh/l
Power density | 10000 | 100 | 3500 | 10000 | 100 | 3500 | 10000 | 100 | 3500 | W/l
Cycle life | 2000 | 500 | 1000 | 10000 | 1000 | 2500 | 20000 | 5000 | 10000 | equivalent full-cycles
Calendar life | 20 | 5 | 12 | 20 | 5 | 12 | 20 | 10 | 15 | a
Depth of discharge | 100 | 84 | 90 | 100 | 84 | 90 | 100 | 84 | 95 | %
Round-trip efficiency | 98 | 80 | 92 | 90 | 81 | 86 | 98 | 80 | 96 | %
Self-discharge | 0.09 | 0.36 | 0.2 | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.05 | % per day
Power dynamic | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 199.5 | 840 | 351.75 | 199.5 | 840 | 577.5 | 472.5 | 1260 | 1050 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
| High Temperature | [5 empty] | Flow
| NaNiCl |  |  | NaS |  |  | Vanadium
| best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 280 | 150 | 215 | 300 | 140 | 250 | 70 | 15 | 45 | Wh/l
Power density | 270 | 150 | 210 | 160 | 120 | 140 | 2 | 0.5 | 1.3 | W/l
Cycle life | 7500 | 1000 | 3000 | 10000 | 1000 | 5000 | 14000 | 12000 | 13000 | equivalent full-cycles
Calendar life | 22 | 8 | 15 | 25 | 10 | 17 | 20 | 5 | 12 | a
Depth of discharge | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Round-trip efficiency | 92 | 80 | 84 | 90 | 70 | 80 | 85 | 60 | 70 | %
Self-discharge | 0.05 | 15 | 5 | 0.05 | 20 | 7 | 0 | 1 | 0.15 | % per day
Power dynamic | 0.1 | < 1 | 0.5 | 3 | 20 | 10 | < 0.001 | 0.02 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 315 | 488 | 399 | 367.5 | 735 | 525 | 315 | 1050 | 346.5 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 1575 | 1312.5 | USD / kW
| Flow |  |  | Inverter
| Zn/Br |  |  | Small (1-30kW) |  |  | Large (>30kW)
| best | worst | ref | best | worst | ref | best | worst | ref | unit
Energy density | 70 | 20 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | Wh/l
Power density | 25 | 0.5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | W/l
Cycle life | 14000 | 300 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
Calendar life | 20 | 5 | 10 | 25 | 10 | 12 | 25 | 19 | 20 | a
Depth of discharge | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | %
Round-trip efficiency | 85 | 60 | 70 | 97 | 93 | 95 | 98 | 98 | 98 | %
Self-discharge | 8 | 33.6 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | % per day
Power dynamic | < 0.001 | 0.02 | 0.01 | - | - | 0.02 | - | - | 0.02 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 525 | 1680 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
Power installation cost | 0 | 0 | 0 | 105 | 290 | 155.4 | 73.5 | 189 | 105 | USD / kW
Note on O4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Beim nächsten Termin nach €/$ Umrechnung fragen

## Pumped Hydro (calc) (hidden)
| Pumped Hydro | [6 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030
| Energy installation cost | 21 | 56 | 72 | 72 | USD / kWh |  | 2016 | 4 | 4 | 4
| Power installation cost | 840 | 1051 | 1112 | 1112 | USD / kW |  | 2016 | 4 | 4 | 4
| Cycle life | 50000 | 50000 | 50000 | 50000 | equivalent full-cycles |  | 2016 | combination | combination | combination
| Calendar life | 60 | 60 | 60 | 60 | a |  | 2016 | combination | combination | combination
| Round-trip efficiency | 80 | 80 | 80 | 80 | % |  | 2016 | combination | combination | combination
| E/P ratio (best) | 4 | 4 | 4 | 4 | h |  | 4 | 4 | 4 | 4
| E/P ratio (worst) | 10 | 10 | 10 | 10 | h |  | 4 | 4 | 4 | 4
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Date |  |  |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | https://sei.info.yorku.ca/files/2013/03/Sauer2.pdf | June 2012
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | https://www.agora-energiewende.de/fileadmin/Projekte/2013/speicher-in-der-energiewende/Agora_Speicherstudie_Web.pdf | September 2014
| 3 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.acatech.de/fileadmin/user_upload/Baumstruktur_nach_Website/Acatech/root/de/Publikationen/Materialien/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015
| 4 | Energy Storage Grand Challenge Cost and Performance Assessment 2022 | PNNL | https://www.pnnl.gov/sites/default/files/media/file/ESGC%20Cost%20Performance%20Report%202022%20PNNL-33283.pdf | August 2022
Percental
Interpolation
Source 1 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2 |  | SEFEP does not expect any improvement/cost reduction of Pumped Hydro
| Energy installation cost | 21 | 28.9075 |  | 43.1023 | 64.2674 |  | USD / kWh | -0.083173
| Power installation cost | 840 | 1010.9997 |  | 1274.5026 | 1606.6838 |  | USD / kW | -0.047413
| Cycle life | 50000 | 50000 |  | 50000 | 50000 |  | equivalent full-cycles | 0
| Calendar life | 60 | 60 |  | 60 | 60 |  | a | 0
| Round-trip efficiency | 80 | 44.1636 |  | 21.0151 | 10 |  | % | 0.13803
Source 2 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 21 | 40.5423 | 66.4011 | 66.4011 | 66.4011 | 66.4011 | USD / kWh | -0.17875 | 0
| Power installation cost | 840 | 840 | 1460.8234 | 1460.8234 | 1460.8234 | 1460.8234 | USD / kW
| Cycle life | 50000 | [5 empty] | equivalent full-cycles
| Calendar life | 60 | 60 | 60 | 60 | 60 | 60 | a | 0 | 0
| Round-trip efficiency | 80 | 80 | 80 | 80 | 80 | 80 | % | 0 | 0
Source 3 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 21 | [5 empty] | USD / kWh | 1
| Power installation cost | 840 | [5 empty] | USD / kW | 1
| Cycle life | 50000 | 54248.1957 | 57669.5773 | 60069.555 | 66515.6029 | 100000 | equivalent full-cycles | -0.020596
| Calendar life | 60 | 62.0655 | 63.6611 | 64.7475 | 67.5455 | 80 | a | -0.0084971
| Round-trip efficiency | 80 | 80 | 80 | 80 | 80 | 80 | % | 0
Source 4 |  | 2016 | 2020 | 2021 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 21 | 56.2743 | 72 | 72 | 72 |  | USD / kWh | -0.27945
| Power installation cost | 840 | 1051.3315 | 1112 | 1112 | 1112 |  | USD / kW | -0.057706
| Cycle life | 50000 |  | Unlimited |  | Unlimited |  | equivalent full-cycles | 1
| Calendar life | 60 |  | 60 |  | 60 |  | a | 1
| Round-trip efficiency | 80 |  | 80 |  | 80 |  | % | 1
| E/P ratio limitation |  | 4 - 10 |  |  |  |  | h

## Pumped Hydro (hidden)
| 2016 |  |  | 2025 |  |  | 2030
Pumped Hydro (calc) | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 2 | 0.2 | 1 | 2 | 0.2 | 1 | 2 | 0.2 | 1 | Wh/l
Power density | 0.2 | 0.1 | 0.15 | 0.2 | 0.1 | 0.15 | 0.2 | 0.1 | 0.15 | W/l
Cycle life | 100000 | 12000 | 50000 | 100000 | 12000 | 50000 | 100000 | 12000 | 50000 | equivalent full-cycles
Calendar life | 100 | 30 | 60 | 100 | 30 | 60 | 100 | 30 | 60 | a
Depth of discharge | 100 | 80 | 90 | 100 | 80 | 90 | 100 | 80 | 90 | %
Round-trip efficiency | 92 | 70 | 80 | 92 | 70 | 80 | 92 | 70 | 80 | %
Self-discharge | 0 | 0.02 | 0.01 | 0 | 0.02 | 0.01 | 0 | 0.02 | 0.01 | % per day
Power dynamic | 15 | 500 | 30 | 15 | 500 | 30 | 15 | 500 | 30 | s to rated power
Planning & Construction Time | 5 | 25 | 15 | 5 | 25 | 15 | 5 | 25 | 15 | a
Energy installation cost | 5.25 | 100 | 21 | 18 | 342.8571 | 72 | 18 | 342.8571 | 72 | USD / kWh
Power installation cost | 525 | 2000 | 840 | 695 | 2647.619 | 1112 | 695 | 2647.619 | 1112 | USD / kW
E/P ratio limitation | 4 | 10 | 7 | 4 | 10 | 7 | 4 | 10 | 7 | h

## CAES (calc) (hidden)
| CAES | [6 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030
| Energy installation cost | 52.5 | 53 | 51 | 49 | USD / kWh |  | 2016 | 2016 | 4 | 4
| Power installation cost | 735 | 735 | 735 | 735 | USD / kW |  | 2016 | 1 | 4 | 4
| Cycle life | 50000 | 75000 | 100000 | 100000 | equivalent full-cycles |  | 2016 | 2 | 4 | 4
| Calendar life | 50 | 50 | 60 | 60 | a |  | 2016 | 2016 | 4 | 4
| Round-trip efficiency | 60 | 64 | 70 | 70 | % |  | 2016 | 2 | 3 | 3
| E/P ratio limitation (best) | 4 | 4 | 4 | 4 | h |  | 3+5 | 3+5 | 3+5 | 3+5
| E/P ratio limitation (reference) | 6 | 6 | 6 | 6 | h |  | 3 | 3 | 3 | 3
| E/P ratio limitation (worst) | 10 | 10 | 10 | 10 | h |  | 5 | 5 | 5 | 5
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Date |  |  |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | https://sei.info.yorku.ca/files/2013/03/Sauer2.pdf | June 2012
| 2 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.acatech.de/fileadmin/user_upload/Baumstruktur_nach_Website/Acatech/root/de/Publikationen/Materialien/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015
| 3 | Technologie-Roadmap Stationäre Energiespeicher 2030 | Fraunhofer ISI | https://www.isi.fraunhofer.de/content/dam/isi/dokumente/cct/lib/TRM-SES.pdf | Dezember 2015
| 4 | World’s largest compressed air energy storage facility commences full operation in China | PV Magazine | https://www.pv-magazine.com/2025/01/10/worlds-largest-compressed-air-energy-storage-facility-commences-full-operation-in-china/ | January 2025
| 5 | Energy Storage Grand Challenge Cost and Performance Assessment 2022 | PNNL | https://www.pnnl.gov/sites/default/files/media/file/ESGC%20Cost%20Performance%20Report%202022%20PNNL-33283.pdf | August 2022
Percental
Interpolation
Source 1 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2
| Energy installation cost | 52.5 | [5 empty] | USD / kWh | 1
| Power installation cost | 735 | 778.7211 |  | 837.0477 | 899.7429 |  | USD / kW | -0.01455
| Cycle life | 50000 | [5 empty] | equivalent full-cycles | 1
| Calendar life | 50 | [5 empty] | a | 1
| Round-trip efficiency | 60 | [5 empty] | % | 1
Source 2 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 52.5 | [5 empty] | USD / kWh | 1
| Power installation cost | 735 | [5 empty] | USD / kW | 1
| Cycle life | 50000 | 74299.7145 | 100000 | 100000 | 100000 | 100000 | equivalent full-cycles | -0.10409 | 0
| Calendar life | 50 | 37.3421 | 30 | 31.7767 | 36.6926 | 40 | a | 0.070376 | -0.029186
| Round-trip efficiency | 60 | 63.9052 | 67 | 67.2177 | 67.7652 | 70 | % | -0.015889 | -0.0016236
Source 3 |  | 2016 | 2015 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 52.5 | [5 empty] | USD / kWh | 1
| Power installation cost | 735 | [5 empty] | USD / kW | 1
| Cycle life | 50000 | [5 empty] | equivalent full-cycles | 1
| Calendar life | 50 | [5 empty] | a | 1
| Round-trip efficiency | 50 | [5 empty] | % | 1
| E/P ratio limitation |  | 4 - 6 |  |  |  |  | 1/h
Source 4 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 52.5 | [5 empty] | USD / kWh | 1
| Power installation cost | 735 | [5 empty] | USD / kW | 1
| Cycle life | 50000 | [5 empty] | equivalent full-cycles | 1
| Calendar life | 50 | [5 empty] | a | 1
| Round-trip efficiency | 60 |  |  | 70 |  |  | % | 1
| E/P ratio limitation |  |  |  | 6
Source 5 |  | 2016 | 2020 | 2021 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 52.5 |  | 52.14 | 50.7203 | 49 |  | USD / kWh | 0.0068776 | 1
| Power installation cost | 735 | [5 empty] | USD / kW | 1
| Cycle life | 50000 | [5 empty] | equivalent full-cycles | 1
| Calendar life | 50 |  | 60 |  | 60 |  | a | -0.026388 | 1
| Round-trip efficiency | 60 | [5 empty] | % | 1
| E/P ratio limitation |  |  | 4 - 10 |  |  |  | h

## CAES (hidden)
| 2016 |  |  | 2025 |  |  | 2030
CAES (calc) | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 6 | 2 | 3 | 6 | 2 | 3 | 6 | 2 | 3 | Wh/l
Power density | 0.6 | 0.2 | 0.4 | 0.6 | 0.2 | 0.4 | 0.6 | 0.2 | 0.4 | W/l
Cycle life | 100000 | 10000 | 50000 | 200000 | 20000 | 100000 | 200000 | 20000 | 100000 | equivalent full-cycles
Calendar life | 100 | 20 | 50 | 120 | 24 | 60 | 120 | 24 | 60 | a
Depth of discharge | 50 | 35 | 40 | 50 | 35 | 40 | 50 | 35 | 40 | %
Round-trip efficiency | 80 | 40 | 60 | 93.3333 | 46.6667 | 70 | 93.3333 | 46.6667 | 70 | %
Self-discharge | 0 | 1 | 0.5 | 0 | 1 | 0.5 | 0 | 1 | 0.5 | % per day
Power dynamic | sec | 900 | 480 | 0 | 900 | 480 | 0 | 900 | 480 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 2 | 84 | 52.5 | 1.9429 | 81.6 | 51 | 1.8667 | 78.4 | 49 | USD / kWh
Power installation cost | 400 | 1050 | 735 | 400 | 1050 | 735 | 400 | 1050 | 735 | USD / kW
E/P ratio limitation | 4 | 10 | 6 | 4 | 10 | 6 | 4 | 10 | 6 | h

## Flywheel (calc) (hidden)
Flywheel | [5 empty] | Sources
| 2016 | 2020 | 2025 | 2030 | unit | Source 2016 | Source 2020 | Source 2025 | Source 2030
Energy installation cost | 3000 | 2655.8784 | 2280.6932 | 1958.5088 | USD / kWh | 2016
Power installation cost | 300 | 265.5878 | 228.0693 | 195.8509 | USD / kW | 2016
Cycle life | 200000 | 225101.762 | 260954.6368 | 302517.945 | equivalent full-cycles | 2016
Calendar life | 20 | 22.5102 | 26.0955 | 30.2518 | a | 2016
Round-trip efficiency | 84 | 85 | 86 | 87 | % | 2016
E/P ratio (best) |  |  |  |  | h
E/P ratio (worst) |  |  |  |  | h
Note: As no reliable data could be found, a simple estimation of 3% annual performance increase / price decrease was used as a reference. For the round-trip efficiency, an increase of 1 percent point per period was assumed.
References
Number of Source | Titel | Authors | Internal File

## Flywheel (hidden)
| 2016 |  |  | 2025 |  |  | 2030
Flywheel (calc) | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 200 | 20 | 80 | 200 | 20 | 80 | 200 | 20 | 80 | Wh/l
Power density | 10000 | 5000 | 7500 | 10000 | 5000 | 7500 | 10000 | 5000 | 7500 | W/l
Cycle life | 1000000 | 100000 | 200000 | 1304773.1838 | 130477.3184 | 260954.6368 | 1512589.7249 | 151258.9725 | 302517.945 | equivalent full-cycles
Calendar life | 25 | 15 | 20 | 32.6193 | 19.5716 | 26.0955 | 37.8147 | 22.6888 | 30.2518 | a
Depth of discharge | 90 | 75 | 85 | 90 | 75 | 85 | 90 | 75 | 85 | %
Round-trip efficiency | 99 | 70 | 84 | 101.3571 | 71.6667 | 86 | 102.5357 | 72.5 | 87 | %
Self-discharge | 20 | 100 | 60 | 20 | 100 | 60 | 20 | 100 | 60 | % per day
Power dynamic | < 0,004 | sec | 0.05 | 0 | 0 | 0.05 | 0 | 0 | 0.05 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 1500 | 6000 | 3000 | 1140.3466 | 4561.3864 | 2280.6932 | 979.2544 | 3917.0177 | 1958.5088 | USD / kWh
Power installation cost | 315 | 1050 | 300 | 239.4728 | 798.2426 | 228.0693 | 205.6434 | 685.4781 | 195.8509 | USD / kW
E/P ratio limitation | [9 empty] | h

## Flooded LA (calc) (hidden)
| Flooded LA | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030
| Energy installation cost | 194.25 | 173 | 154 | 140 | USD / kWh |  | ref 2016 | 2 | 2 | 2
| Power installation cost | 0 | 0 | 0 | 0 | USD / kW |  | ref 2016 | 1 | 1 | 1
| Cycle life | 1500 | 1800 | 2500 | 3000 | equivalent full-cycles |  | ref 2016 | Combination | Combination | Combination
| Calendar life | 9 | 10 | 12 | 15 | a |  | ref 2016 | Combination | Combination | Combination
| Round-trip efficiency | 82 | 82 | 82 | 82 | % |  | ref 2016 | Combination | Combination | Combination
| E/P ratio limitation (best) | 1 | 1 | 1 | 1 | h |  | 7 | 7 | 7 | 7
| E/P ratio limitation (worst) | 10 | 10 | 10 | 10 | h |  | ISEA | ISEA | ISEA | ISEA
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Date |  | Type |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | https://sei.info.yorku.ca/files/2013/03/Sauer2.pdf | June 2012 |  | lead-acid batteries
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | https://www.agora-energiewende.de/fileadmin/Projekte/2013/speicher-in-der-energiewende/Agora_Speicherstudie_Web.pdf | September 2014 |  | lead-acid batteries
| 3 | Batteriespeicher in der Nieder- und Mittelspannungsebene | VDE | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | Mai 2015 |  | lead-acid batteries
| 4 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.acatech.de/fileadmin/user_upload/Baumstruktur_nach_Website/Acatech/root/de/Publikationen/Materialien/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015 |  | lead-acid batteries
| 5 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | advanced lead-acid
| 6 | Energy Storage Grand Challenge Cost and Performance Assessment 2022 | PNNL | https://www.pnnl.gov/sites/default/files/media/file/ESGC%20Cost%20Performance%20Report%202022%20PNNL-33283.pdf | August 2022 |  | lead-acid batteries
| 7 | Analyse und Optimierung der Zuverlässigkeit und Effizienz von hybriden Batteriespeichern am Beispiel von M5BAT | Koltermann | https://publications.rwth-aachen.de/record/1015017/files/1015017.pdf | February 2025 |  | lead-acid batteries
Percental
Interpolation
Source 1 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2
| Energy installation cost | 194.25 | 152.6397 |  | 112.9277 | 83.5476 |  | USD / kWh | 0.058486
| Power installation cost | 0 | 0 |  | 0 | 64.2674 |  | USD / kW
| Cycle life | 1500 | 1870.8194 |  | 2465.7986 | 3250 |  | equivalent full-cycles | -0.056781
| Calendar life | 9 | 10.4142 |  | 12.4985 | 15 |  | a | -0.037161
| Round-trip efficiency | 82 | 82 |  | 82 | 82 |  | % | 0
Source 2 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 194.25 | 173.4733 | 159.3625 | 153.6562 | 140.2683 | 132.8021 | USD / kWh | 0.027884 | 0.018067
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 1500 | [5 empty] | equivalent full-cycles
| Calendar life | 9 | 9.5585 | 10 | 10 | 10 | 10 | a | -0.015165 | 0
| Round-trip efficiency | 82 | 80.8511 | 80 | 80 | 80 | 80 | % | 0.0035213 | 0
Source 3 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 194.25 | [5 empty] | USD / kWh | 1
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 1500 | 3250 |  | 3250 | 3250 |  | equivalent full-cycles | 1 | 0
| Calendar life | 9 | 15 |  | 15 | 15 |  | a | 1 | 0
| Round-trip efficiency | 80 | 81 |  | 81 | 81 |  | % | 1 | 0
Source 4 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 194.25 | [5 empty] | USD / kWh | 1
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 1500 | 2008.4544 | 2500 | 2500 | 2500 |  | equivalent full-cycles | -0.075704 | 0
| Calendar life | 9 | 11.1045 | 13 | 13.5425 | 15 |  | a | -0.053936 | -0.020653
| Round-trip efficiency | 82 | 84.8209 | 87 | 87.5668 | 89 |  | % | -0.0084914 | -0.0032522
Source 5 |  | 2016 | 2017 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 194.25 | 550 | 500 | 469.2182 | 400.3014 |  | USD / kWh | -0.29718 | 0.031271
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 1500 | [5 empty] | equivalent full-cycles
| Calendar life | 9 | [5 empty] | a
| Round-trip efficiency | 82 | [5 empty] | %
Source 6 |  | 2016 | 2020 | 2021 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 194.25 | 315.3786 | 356 | 338.5806 | 318 |  | USD / kWh | -0.1288 | 0.012464
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 1500 |  | 1500 |  | 1500 |  | equivalent full-cycles
| Calendar life | 9 |  | 12 |  | 12 |  | a
| Round-trip efficiency | 82 |  | 75 |  | 75 |  | %
Source 7 |  | 2016 | 2020 | 2021 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 194.25 | [5 empty] | USD / kWh | 1
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 1500 | [5 empty] | equivalent full-cycles
| Calendar life | 9 | [5 empty] | a
| Round-trip efficiency | 82 | [5 empty] | %
| E/P ratio |  |  |  | > 1 |  |  | h

## Flooded LA (hidden)
| 2016 |  |  | 2025 |  |  | 2030
Flooded LA (calc) | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 100 | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | Wh/l
Power density | 700 | 10 | 350 | 700 | 10 | 350 | 700 | 10 | 350 | W/l
Cycle life | 2500 | 250 | 1500 | 4166.6667 | 416.6667 | 2500 | 5000 | 500 | 3000 | equivalent full-cycles
Calendar life | 15 | 3 | 9 | 20 | 4 | 12 | 25 | 5 | 15 | a
Depth of discharge | 50 | 60 | 50 | 50 | 60 | 50 | 50 | 60 | 50 | %
Round-trip efficiency | 92 | 75 | 82 | 92 | 75 | 82 | 92 | 75 | 82 | %
Self-discharge | 0.09 | 0.4 | 0.25 | 0.09 | 0.4 | 0.25 | 0.09 | 0.4 | 0.25 | % per day
Power dynamic | 0.003 | 0.01 | 0.006 | 0.003 | 0.01 | 0.006 | 0.003 | 0.01 | 0.006 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 105 | 472.5 | 194.25 | 83.2432 | 374.5946 | 154 | 75.6757 | 340.5405 | 140 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
E/P ratio limitation | 1 | 10 | 5.5 | 1 | 10 | 5.5 | 1 | 10 | 5.5 | h

## VRLA (calc) (hidden)
| LA | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030
| Energy installation cost | 210 | 179 | 154 | 140 | USD / kWh |  | ref 2016 | 2 | 2 | 2
| Power installation cost | 0 | 0 | 0 | 0 | USD / kW |  | ref 2016 | 1 | 1 | 1
| Cycle life | 1500 | 1800 | 2500 | 3000 | equivalent full-cycles |  | ref 2016 | Combination | Combination | Combination
| Calendar life | 9 | 10 | 12 | 15 | a |  | ref 2016 | Combination | Combination | Combination
| Round-trip efficiency | 82 | 82 | 82 | 82 | % |  | ref 2016 | Combination | Combination | Combination
| E/P ratio limitation (best) | 1 | 1 | 1 | 1 | h |  | 7 | 7 | 7 | 7
| E/P ratio limitation (worst) | 10 | 10 | 10 | 10 | h |  | ISEA | ISEA | ISEA | ISEA
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Date |  | Type |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | https://sei.info.yorku.ca/files/2013/03/Sauer2.pdf | June 2012 |  | lead-acid batteries
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | http://www.speicherinitiative.at/assets/Uploads/19-AgoraEnergiewende-Speicherstudie-Langfassung.pdf | September 2014 |  | lead-acid batteries
| 3 | Batteriespeicher in der Nieder- und Mittelspannungsebene | VDE | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | Mai 2015 |  | lead-acid batteries
| 4 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.acatech.de/fileadmin/user_upload/Baumstruktur_nach_Website/Acatech/root/de/Publikationen/Materialien/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015 |  | lead-acid batteries
| 5 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | advanced lead-acid
| 6 | Energy Storage Grand Challenge Cost and Performance Assessment 2022 | PNNL | https://www.pnnl.gov/sites/default/files/media/file/ESGC%20Cost%20Performance%20Report%202022%20PNNL-33283.pdf | August 2022 |  | lead-acid batteries
| 7 | Analyse und Optimierung der Zuverlässigkeit und Effizienz von hybriden Batteriespeichern am Beispiel von M5BAT | Koltermann | https://publications.rwth-aachen.de/record/1015017/files/1015017.pdf | February 2025 |  | lead-acid batteries
Percental
Interpolation
Source 1 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2
| Energy installation cost | 210 | 161.3809 |  | 116.1162 | 83.5476 |  | USD / kWh | 0.063715
| Power installation cost | 0 | 0 |  | 0 | 64.2674 |  | USD / kW
| Cycle life | 1500 | 1870.8194 |  | 2465.7986 | 3250 |  | equivalent full-cycles | -0.056781
| Calendar life | 9 | 10.4142 |  | 12.4985 | 15 |  | a | -0.037161
| Round-trip efficiency | 82 | 82 |  | 82 | 82 |  | % | 0
Source 2 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 210 | 179.3673 | 159.3625 | 153.6562 | 140.2683 | 132.8021 | USD / kWh | 0.038651 | 0.018067
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 1500 | [5 empty] | equivalent full-cycles
| Calendar life | 9 | 9.5585 | 10 | 10 | 10 | 10 | a | -0.015165 | 0
| Round-trip efficiency | 82 | 80.8511 | 80 | 80 | 80 | 80 | % | 0.0035213 | 0
Source 3 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 210 | [5 empty] | USD / kWh | 1
| Power installation cost | 0 | [5 empty] | USD / kW | #DIV/0!
| Cycle life | 1500 | 3250 |  | 3250 | 3250 |  | equivalent full-cycles | 1 | 0
| Calendar life | 9 | 15 |  | 15 | 15 |  | a | 1 | 0
| Round-trip efficiency | 80 | 81 |  | 81 | 81 |  | % | 1 | 0
Source 4 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 210 | [5 empty] | USD / kWh | 1
| Power installation cost | 0 | [5 empty] | USD / kW | #DIV/0!
| Cycle life | 1500 | 2008.4544 | 2500 | 2500 | 2500 |  | equivalent full-cycles | -0.075704 | 0
| Calendar life | 9 | 11.1045 | 13 | 13.5425 | 15 |  | a | -0.053936 | -0.020653
| Round-trip efficiency | 82 | 84.8209 | 87 | 87.5668 | 89 |  | % | -0.0084914 | -0.0032522
Source 5 |  | 2016 | 2017 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 210 | 550 | 500 | 469.2182 | 400.3014 |  | USD / kWh | -0.27214 | 0.031271
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 1500 | [5 empty] | equivalent full-cycles
| Calendar life | 9 | [5 empty] | a
| Round-trip efficiency | 82 | [5 empty] | %
Source 6 |  | 2016 | 2020 | 2021 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 210 | 320.3346 | 356 | 338.5806 | 318 |  | USD / kWh | -0.11134 | 0.012464
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 1500 |  | 1500 |  | 1500 |  | equivalent full-cycles
| Calendar life | 9 |  | 12 |  | 12 |  | a
| Round-trip efficiency | 82 |  | 75 |  | 75 |  | %
Source 7 |  | 2016 | 2020 | 2021 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 0 | [5 empty] | USD / kWh | #DIV/0!
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 2016 | [5 empty] | equivalent full-cycles
| Calendar life | 210 | [5 empty] | a
| Round-trip efficiency | 0 | [5 empty] | %
| E/P ratio |  |  |  | > 1 |  |  | h

## VRLA (hidden)
| 2016 |  |  | 2025 |  |  | 2030
VRLA (calc) | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 100 | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | Wh/l
Power density | 700 | 10 | 350 | 700 | 10 | 350 | 700 | 10 | 350 | W/l
Cycle life | 2500 | 250 | 1500 | 4166.6667 | 416.6667 | 2500 | 5000 | 500 | 3000 | equivalent full-cycles
Calendar life | 15 | 3 | 9 | 20 | 4 | 12 | 25 | 5 | 15 | a
Depth of discharge | 50 | 60 | 50 | 50 | 60 | 50 | 50 | 60 | 50 | %
Round-trip efficiency | 92 | 75 | 82 | 92 | 75 | 82 | 92 | 75 | 82 | %
Self-discharge | 0.09 | 0.4 | 0.25 | 0.09 | 0.4 | 0.25 | 0.09 | 0.4 | 0.25 | % per day
Power dynamic | 0.003 | 0.01 | 0.006 | 0.003 | 0.01 | 0.006 | 0.003 | 0.01 | 0.006 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 105 | 472.5 | 210 | 77 | 346.5 | 154 | 70 | 315 | 140 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
E/P ratio limitation | 1 | 10 | 5.5 | 1 | 10 | 5.5 | 1 | 10 | 5.5 | h

## Li-Ion (NMC) (calc) (hidden)
| Li-Ion (NMC) | [7 empty] | Sources
|  | 2016 | 2025 | 2030 | unit |  | Source 2016 | Source 2025 | Source 2030
| Energy installation cost | 420 | 210 | 143 | USD / kWh |  | ref 2016 | 11+12 | 11+12
| Power installation cost | 0 | 0 | 0 | USD / kW |  | ref 2016 | 1 | 1
| Cycle life | 2000 | 2000 | 2000 | equivalent full-cycles |  | ref 2016 | combination | combination
| Calendar life | 12 | 20 | 20 | a |  | ref 2016 | 10 | 10
| Round-trip efficiency | 92 | 92 | 92 | % |  | ref 2016 | combination | combination
| E/P ratio limitation (best) | 0.33333 | 0.33333 | 0.33333 | 1/h |  | 13 | 13 | 13
| E/P ratio limitation (worst) | 1 | 1 | 1 | h |  | 13 | 13 | 13
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Date |  | Type | Comment |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | https://sei.info.yorku.ca/files/2013/03/Sauer2.pdf | June 2012 |  | lithium-ion batteries
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | https://www.agora-energiewende.de/fileadmin/Projekte/2013/speicher-in-der-energiewende/Agora_Speicherstudie_Web.pdf | September 2014 |  | lithium-ion batteries
| 3 | Batteriespeicher in der Nieder- und Mittelspannungsebene | VDE | https://www.vde.com/resource/blob/2319156/adacf7890ac200902769bf38f742d9fb/vde-studie-batteriespeicher-in-der-nieder-und-mittelspannungsebene-data.pdf | Mai 2015 |  | lithium-ion batteries
| 4 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | https://energiesysteme-zukunft.de/fileadmin/user_upload/Publikationen/PDFs/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015 |  | lithium-ion batteries
| 5 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | NMC
| 6 | The Technical Advantages of Lithium Titanate (LTO) Cells for Enhanced Energy Efficiency |  | https://www.global-batteries.com/the-technical-advantages-of-lithium-titanate-lto-cells-for-enhanced-energy-efficiency | April 2025 |  | NMC
| 7 | What are the advantages of lithium titanate batteries? |  | https://www.youth-battery.com/what-are-the-advantages-of-lithium-titanate-batteries/ | April 2025 |  | NMC
| 8 | Batteries for electric cars: Sodium cells on the advance? | Christoph M. Schwarzer | https://www.heise.de/hintergrund/Batteries-for-electric-cars-Sodium-cells-on-the-advance-9193645.html | June 2023 |  | NMC
| 9 | Industrial batteries. Chapter 3 (PART 2/2). Lithium-Ion battery types |  | https://norwatt.es/noticia-industrial-batteries--chapter-3-part-2-2--lithium-ion-battery-types-es.html | June 2020 |  | NMC
| 10 | A Formulation Model to Compute the Life Cycle Environmental Impact of NiZn Batteries from Cradle to Grave | Ashwani Kumar Malviya, Mehdi Zarehparast Malekzadeh, Jinping Li, Boyang Li, Francisco Enrique Santarremigia, Gemma Dolores Molero, Ignacio Villalba Sanchis, Víctor Yepes | https://www.mdpi.com/1996-1073/17/11/2751 | 2024 |  | NMC
| 11 | Cost modeling for the GWh-scale production of modern lithium-ion battery cells | Lechner, Maximilian et al. | https://www.nature.com/articles/s44172-024-00306-0 | 2024 |  | NMC
| 12 | BNEF energy storage outlook 2023 | BNEF | https://about.bnef.com/ | 2023 |  | LFP | Used as a reference to seperate cell from system costs (see calculation in supporting documentation)
| 13 | Lithium-Ion Battery Roadmap – Industrialization Perspectives Toward 2030 | Fraunhofer ISI | https://www.isi.fraunhofer.de/content/dam/isi/dokumente/cct/2023/Fraunhofer-ISI_LIB-Roadmap-2023.pdf | December 2023 |  | lithium-ion batteries
Percental
Interpolation
Source 1 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2
| Energy installation cost | 420 | 377.529 |  | 330.4278 | 289.2031 |  | USD / kWh | 0.0263
| Power installation cost | 0 | 0 |  | 0 | 64.2674 |  | USD / kW
| Cycle life | 2000 | 2800.8018 |  | 4266.7566 | 6500 |  | equivalent full-cycles | -0.087835
| Calendar life | 12 | 13.8857 |  | 16.6647 | 20 |  | a | -0.037161
| Round-trip efficiency | 92 |  |  |  | 89 |  | % | 0.0023652
Source 2 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 420 | 445.0469 | 464.8074 | 442.9207 | 392.6073 | 365.2058 | USD / kWh | -0.014587 | 0.023828
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 2000 | [5 empty] | equivalent full-cycles
| Calendar life | 12 | 13.632 | 15 | 15.8884 | 18.3463 | 20 | a | -0.032391 | -0.029186
| Round-trip efficiency | 92 |  | 90 | 90 | 90 | 90 | % | 0.0031349 | 0
Source 3 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 420 | 199.778 |  | 160.9323 | 129.6399 |  | USD / kWh | 0.080536 | 0.042323
| Power installation cost | 0 | [5 empty] | USD / kW | #DIV/0!
| Cycle life | 2000 | 6500 |  | 6500 | 6500 |  | equivalent full-cycles | -0.087835 | 0
| Calendar life | 12 | 20 |  | 20 | 20 |  | a | -0.037161 | 0
| Round-trip efficiency | 92 | 87.5 |  | 87.5 | 87.5 |  | % | 0.0035757 | 0
Source 4 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 420 | 457.1945 | 487.2364 | 473.0983 | 439.5219 | 327.414 | USD / kWh | -0.02144 | 0.014615
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 2000 | 4091.9095 | 7000 | 7285.1339 | 8049.822 | 12000 | equivalent full-cycles | -0.19598 | -0.020163
| Calendar life | 12 | 14.6427 | 17 | 17.4398 | 18.5899 | 24 | a | -0.051017 | -0.012854
| Round-trip efficiency | 92 |  | 87 | 87.2188 | 87.768 | 90 | % | 0.0079511 | -0.0012564
Source 5 |  | 2016 | 2017 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 420 | 500 | 300 | 213.4136 | 91.0907 |  | USD / kWh | -0.044552 | 0.15657
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 2000 | [5 empty] | equivalent full-cycles
| Calendar life | 12 | [5 empty] | a
| Round-trip efficiency | 92 | [5 empty] | %
Source 6 |  | 2016 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 420 | 150 | 84.6584 | USD / kWh | 0.1081
| Power installation cost | 0 |  |  | USD / kW
| Cycle life | 2000 | 4000 | 5878.938 | equivalent full-cycles | -0.08006
| Calendar life | 12 |  |  | a
| Round-trip efficiency | 92 |  |  | %
Source 7 |  | 2016 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 420 | 280 | 223.5268 | USD / kWh | 0.044052
| Power installation cost | 0 |  |  | USD / kW
| Cycle life | 2000 | 1500 | 1500 | equivalent full-cycles
| Calendar life | 12 |  |  | a
| Round-trip efficiency | 92 |  |  | %
Source 8 |  | 2016 | 2023 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 420 | 151 | 112.7306 | 54.2881 | USD / kWh | 0.13596
| Power installation cost | 0 |  |  |  | USD / kW
| Cycle life | 2000 |  |  |  | equivalent full-cycles | 1
| Calendar life | 12 |  |  |  | a
| Round-trip efficiency | 92 |  |  |  | %
Source 9 |  | 2016 | 2020 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 420 |  |  |  | USD / kWh | 1
| Power installation cost | 0 |  |  |  | USD / kW
| Cycle life | 2000 | 1500 | 1500 | 1500 | equivalent full-cycles | 0.031459
| Calendar life | 12 | >10 | >10 | >10 | a
| Round-trip efficiency | 92 |  |  |  | %
Source 10 |  | 2016 | 2024 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 420 |  |  |  | USD / kWh
| Power installation cost | 0 |  |  |  | USD / kW
| Cycle life | 2000 |  |  |  | equivalent full-cycles
| Calendar life | 12 | 20 | 21.3187 | 29.3371 | a | -0.065936
| Round-trip efficiency | 92 |  |  |  | %
Source 11+12 |  | 2016 | 2024 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 420 |  | 210 | 142.883 | USD / kWh | 0.074125
| Power installation cost | 0 |  |  |  | USD / kW
| Cycle life | 2000 |  |  |  | equivalent full-cycles
| Calendar life | 12 |  |  |  | a | 1
| Round-trip efficiency | 92 |  |  |  | %
Source 13 |  | 2016 | 2023 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 420 |  |  |  | USD / kWh | 1
| Power installation cost | 0 |  |  |  | USD / kW
| Cycle life | 2000 |  |  |  | equivalent full-cycles
| Calendar life | 12 |  |  |  | a | 1
| Round-trip efficiency | 92 |  |  |  | %
| E/P ratio limitation |  | 0.33 - 1 |  |  | h

## Li-Ion (NMC) (hidden)
| 2016 |  |  | 2025 |  |  | 2030
Li-Ion (NMC) (calc) | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 735 | 200 | 468 | 735 | 200 | 468 | 735 | 200 | 468 | Wh/l
Power density | 10000 | 100 | 3500 | 10000 | 100 | 3500 | 10000 | 100 | 3500 | W/l
Cycle life | 4000 | 500 | 2000 | 4000 | 500 | 2000 | 4000 | 500 | 2000 | equivalent full-cycles
Calendar life | 20 | 5 | 12 | 33.3333 | 8.3333 | 20 | 33.3333 | 8.3333 | 20 | a
Depth of discharge | 100 | 84 | 90 | 100 | 84 | 90 | 100 | 84 | 90 | %
Round-trip efficiency | 98 | 81 | 92 | 98 | 81 | 92 | 98 | 81 | 92 | %
Self-discharge | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.1 | % per day
Power dynamic | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 199.5 | 840 | 420 | 99.75 | 420 | 210 | 67.925 | 286 | 143 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
E/P ratio limitation | 0.33333 | 1 | 0.66667 | 0.33333 | 1 | 0.66667 | 0.33333 | 1 | 0.66667 | h
Note on H10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Warum sinkt die RTE über die Zeit?

## Li-Ion (LFP) (calc) (hidden)
| Li-Ion (LFP) | [7 empty] | Sources
|  | 2016 | 2025 | 2030 | unit |  | Source 2016 | Source 2025 | Source 2030
| Energy installation cost | 577.5 | 195 | 107 | USD / kWh |  | ref 2016 | 16+17 | 16+17
| Power installation cost | 0 | 0 | 0 | USD / kW |  | ref 2016 | combination | combination
| Cycle life | 2500 | 5000 | 7500 | equivalent full-cycles |  | ref 2016 | combination | combination
| Calendar life | 12 | 17 | 20 | a |  | ref 2016 | combination | combination
| Round-trip efficiency | 86 | 92 | 94 | % |  | ref 2016 | combination | combination
| E/P ratio limitation (best) | 0.33333 | 0.33333 | 0.33333 | 1/h |  | 18 | 18 | 18
| E/P ratio limitation (worst) | 1 | 1 | 1 | h |  | 18 | 18 | 18
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Date |  | Type |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | https://sei.info.yorku.ca/files/2013/03/Sauer2.pdf | June 2012 |  | lithium-ion batteries
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | https://www.agora-energiewende.de/fileadmin/Projekte/2013/speicher-in-der-energiewende/Agora_Speicherstudie_Web.pdf | September 2014 |  | lithium-ion batteries
| 3 | Batteriespeicher in der Nieder- und Mittelspannungsebene | VDE | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | Mai 2015 |  | lithium-ion batteries
| 4 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.acatech.de/fileadmin/user_upload/Baumstruktur_nach_Website/Acatech/root/de/Publikationen/Materialien/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015 |  | lithium-ion batteries
| 5 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | LFP
| 6 | The Unmatched Advantages of Lithium Iron Phosphate (LFP) Batteries‌ |  | https://lanpwr.com/blogs/news/the-unmatched-advantages-of-lithium-iron-phosphate-lfp-batteries | May 2025 |  | LFP
| 7 | Lithium Ferro Phosphate (LFP) Battery Technology | Usman Noor | https://8msolar.com/lithium-ferro-phosphate-lfp-battery-technology | July 2025 |  | LFP
| 8 | How Long Do Lithium Iron Phosphate (LiFePO4) Batteries Last? | Victoria Chen-Englert | https://www.qurator.com/blog/how-long-do-lithium-iron-phosphate-batteries-last | February 2024 |  | LFP
| 9 | Electricity Storage and Renewables: Costs and Markets to 2030 | IRENA | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2017/Oct/IRENA_Electricity_Storage_Costs_2017.pdf | October 2017 |  | lithium-ion batteries
| 10 | Lithium-Ion Battery Pack Prices See Largest Drop Since 2017, Falling to $115 per Kilowatt-Hour: BloombergNEF | BloombergNEF | https://about.bnef.com/insights/commodities/lithium-ion-battery-pack-prices-see-largest-drop-since-2017-falling-to-115-per-kilowatt-hour-bloombergnef/ | December 2024 |  | lithium-ion batteries
| 11 | Cost Projections for Utility-Scale Battery Storage: 2023 Update | National Renewable Energy Laboratory (Cole, Karmakar) | https://docs.nrel.gov/docs/fy23osti/85332.pdf | June 2023 |  | lithium-ion batteries
| 12 | Findings from Storage Innovations 2030 Lithium-ion Batteries | U.S. DoE (Dufek, Durvasulu, Mosier, Balliet, Willey, Bakhtian) | https://www.energy.gov/sites/default/files/2023-09/2_Technology%20Strategy%20Assessment%20-%202%20Lithium-ion_508.pdf | July 2023 |  | LFP
| 13 | Utility-Scale Battery Storage | NREL | https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage | February 2025 |  | lithium-ion batteries
| 14 | A comprehensive review on the techno-economic analysis of electrochemical energy storage systems: Technologies, applications, benefits and trends | Huang, Zeng, Lashari, Xie | https://www.sciencedirect.com/science/article/pii/S2950264025000103#bib66 | February 2025 |  | lithium-ion batteries
| 15 | EIA | EIA | eia.gov/analysis/studies/powerplants/capitalcost/pdf/capital_cost_AEO2025.pdf | 2023 |  | li ion
| 16 | Energy Storage Market Outlook 2023 | BNEF | https://www.linkedin.com/posts/adamerkienok_bess-pv-activity-7192498064488599554-IMse/ | 2023 |  | lithium ion
| 17 | Critically assessing sodium-ion technology roadmaps and scenarios for techno-economic competitiveness against lithium-ion batteries | Yao, Benson, Chueh | https://www.nature.com/articles/s41560-024-01701-9.pdf | January 2025 |  | LFP
| 18 | Lithium-Ion Battery Roadmap – Industrialization Perspectives Toward 2030 | Fraunhofer ISI | https://www.isi.fraunhofer.de/content/dam/isi/dokumente/cct/2023/Fraunhofer-ISI_LIB-Roadmap-2023.pdf | December 2023 |  | lithium-ion batteries
Percental
Interpolation
Source 1 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2
| Energy installation cost | 577.5 | 473.9559 |  | 370.229 | 289.2031 |  | USD / kWh | 0.048198
| Power installation cost | 0 | 0 |  | 0 | 64.2674 |  | USD / kW | 0
| Cycle life | 2500 | 3284.7614 |  | 4620.7087 | 6500 |  | equivalent full-cycles | -0.070634
| Calendar life | 12 | 13.8857 |  | 16.6647 | 20 |  | a | -0.037161
| Round-trip efficiency | 86 | 86.8467 |  | 87.9167 | 89 |  | % | -0.0024522
Source 2 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 577.5 | 510.127 | 464.8074 | 442.9207 | 392.6073 | 365.2058 | USD / kWh | 0.030536 | 0.023828
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 2500 | [5 empty] | equivalent full-cycles
| Calendar life | 12 | 13.632 | 15 | 15.8884 | 18.3463 | 20 | a | -0.032391 | -0.029186
| Round-trip efficiency | 86 | 88.2634 | 90 | 90 | 90 | 90 | % | -0.0065158 | 0
Source 3 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 577.5 | 199.778 |  | 160.9323 | 129.6399 |  | USD / kWh | 0.10121 | 0.042323
| Power installation cost | 0 | [5 empty] | USD / kW | #DIV/0!
| Cycle life | 2500 | 6500 |  | 6500 | 6500 |  | equivalent full-cycles | -0.070634 | 0
| Calendar life | 12 | 20 |  | 20 | 20 |  | a | -0.037161 | 0
| Round-trip efficiency | 86 | 87.5 |  | 87.5 | 87.5 |  | % | -0.0012359 | 0
Source 4 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 577.5 | 524.051 | 487.2364 | 473.0983 | 439.5219 | 327.414 | USD / kWh | 0.023987 | 0.014615
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 2500 | 4502.5535 | 7000 | 7285.1339 | 8049.822 | 12000 | equivalent full-cycles | -0.15846 | -0.020163
| Calendar life | 12 | 14.6427 | 17 | 17.4398 | 18.5899 | 24 | a | -0.051017 | -0.012854
| Round-trip efficiency | 86 | 86.57 | 87 | 87.2188 | 87.768 | 90 | % | -0.0016529 | -0.0012564
Source 5 |  | 2016 | 2017 | 2020 | 2025 | 2030 |  | unit
| Energy installation cost | 577.5 | 430 | 440 | 313.2049 | 222.9484 |  | USD / kWh | 0.25541 | 0.065724
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 2500 | [5 empty] | equivalent full-cycles
| Calendar life | 12 | [5 empty] | a
| Round-trip efficiency | 86 | [5 empty] | %
Source 6 |  | 2016 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 577.5 | 500 | 461.5324 | USD / kWh | 0.015884
| Power installation cost | 0 |  |  | USD / kW
| Cycle life | 2500 | 4000 | 5193.4982 | equivalent full-cycles | -0.05361
| Calendar life | 12 | 20 | 26.5631 | a | -0.0584
| Round-trip efficiency | 86 |  |  | %
Source 7 |  | 2016 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 577.5 |  |  | USD / kWh
| Power installation cost | 0 |  |  | USD / kW
| Cycle life | 2500 | 4500 | 6237.7874 | equivalent full-cycles | -0.067489
| Calendar life | 12 | 12.5 | 12.7867 | a | -0.0045461
| Round-trip efficiency | 86 | 94.5 | 94.5 | % | -0.010528
Source 8 |  | 2016 | 2024 | 2030 | unit | X1 | X2
| Energy installation cost | 577.5 |  |  | USD / kWh
| Power installation cost | 0 |  |  | USD / kW
| Cycle life | 2500 | 5750 | 10738.997 | equivalent full-cycles | -0.10973
| Calendar life | 12 | 7.5 | 7.5 | a | 0.057058
| Round-trip efficiency | 86 |  |  | %
Source 9 |  | 2016 | 2020 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 578 |  |  | 224 | USD / kWh | 1
| Power installation cost | 0 |  |  |  | USD / kW
| Cycle life | 2500 |  |  | 4774 | equivalent full-cycles
| Calendar life | 12 |  |  | 18 | a
| Round-trip efficiency | 92 |  |  | 94 | %
Source 10 |  | 2016 | 2020 | 2024 | 2030 | unit | X1 | X2 | notes
| Energy installation cost |  |  | 115 |  | USD / kWh |  |  | battery pack price 2024
| Power installation cost |  |  |  |  | USD / kW
| Cycle life |  |  |  |  | equivalent full-cycles
| Calendar life |  |  |  |  | a
| Round-trip efficiency |  |  |  |  | %
Source 11 |  | 2016 | 2020 | 2022 | 2030 | unit | X1 | X2 | notes
| Energy installation cost | 577.5 |  | 482 | 245-403 | USD / kWh | 1 |  | 4-hour Storage costs
| Power installation cost | 0 |  |  |  | USD / kW
| Cycle life | 2500 |  |  |  | equivalent full-cycles
| Calendar life | 12 |  |  |  | a
| Round-trip efficiency | 86 |  | 85 |  | %
Source 12 |  | 2016 | 2020 | 2022 | 2030 | unit | X1 | X2
| Energy installation cost | 577.5 |  |  | 106.22 | USD / kWh | 1
| Power installation cost | 0 |  |  |  | USD / kW
| Cycle life | 2500 |  |  | 2640 | equivalent full-cycles
| Calendar life | 12 |  |  | 16 | a
| Round-trip efficiency | 86 |  |  | 85 | %
Source 13 |  | 2016 | 2023 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 577.5 | 301.49 | 250.3927 | 157.3961 | USD / kWh | 0.088673
| Power installation cost | 0 | 1798.94 |  |  | USD / kW
| Cycle life | 2500 |  |  |  | equivalent full-cycles
| Calendar life | 12 |  |  |  | a
| Round-trip efficiency | 86 | 85 |  |  | %
Source 14 |  | 2016 | 2020 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost |  |  | 400-1300 |  | USD / kWh
| Power installation cost |  |  |  |  | USD / kW
| Cycle life |  |  | 1000–5000 |  | equivalent full-cycles
| Calendar life |  |  |  |  | a
| Round-trip efficiency |  |  | 85-95 |  | %
Source 15 |  | 2016 | 2023 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 259 | 111 | 78 |  | USD / kWh
| Power installation cost |  |  |  |  | USD / kW
| Cycle life |  |  |  |  | equivalent full-cycles
| Calendar life |  |  |  |  | a
| Round-trip efficiency |  |  |  |  | %
Source 16+17 |  | 2016 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 577.5 | 195 | 106.6794 | USD / kWh | 0.11364
| Power installation cost | 0 |  |  | USD / kW
| Cycle life | 2500 |  |  | equivalent full-cycles
| Calendar life | 12 |  |  | a
| Round-trip efficiency | 86 |  |  | %
Source 18 |  | 2016 | 2023 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 577.5 |  |  |  | USD / kWh | 1
| Power installation cost | 0 |  |  |  | USD / kW
| Cycle life | 2500 |  |  |  | equivalent full-cycles
| Calendar life | 12 |  |  |  | a | 1
| Round-trip efficiency | 86 |  |  |  | %
| E/P ratio limitation |  | 0.33 - 1 |  |  | h

## Li-Ion (LFP) (hidden)
| 2016 |  |  | 2025 |  |  | 2030
Li-Ion (LFP) (calc) | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 620 | 200 | 350 | 620 | 200 | 350 | 620 | 200 | 350 | Wh/l
Power density | 10000 | 100 | 3500 | 10000 | 100 | 3500 | 10000 | 100 | 3500 | W/l
Cycle life | 10000 | 1000 | 2500 | 20000 | 2000 | 5000 | 30000 | 3000 | 7500 | equivalent full-cycles
Calendar life | 20 | 5 | 12 | 28.3333 | 7.0833 | 17 | 33.3333 | 8.3333 | 20 | a
Depth of discharge | 100 | 84 | 90 | 100 | 84 | 90 | 100 | 84 | 90 | %
Round-trip efficiency | 90 | 81 | 86 | 96.2791 | 86.6512 | 92 | 98.3721 | 88.5349 | 94 | %
Self-discharge | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.1 | % per day
Power dynamic | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 199.5 | 840 | 577.5 | 67.3636 | 283.6364 | 195 | 36.9636 | 155.6364 | 107 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
E/P ratio limitation | 0.33333 | 1 | 0.66667 | 0.33333 | 1 | 0.66667 | 0.33333 | 1 | 0.66667 | h

## Li-Ion (Titanate) (calc) (hidden)
| Li-Ion (Titanate) | [8 empty] | Sources
|  | 2016 | 2025 | 2030 | unit |  |  | Source 2016 | Source 2025 | Source 2030
| Energy installation cost | 1050 | 422 | 254 | USD / kWh |  |  | ref 2016 | 9+10 | 9+10
| Power installation cost | 0 | 78 | 50 | USD / kW |  |  | ref 2016 | 1 | 1
| Cycle life | 10000 | 17500 | 24000 | equivalent full-cycles |  |  | ref 2016 | 7 | 7
| Calendar life | 15 | 17 | 20 | a |  |  | ref 2016 | combination | combination
| Round-trip efficiency | 96 | 96 | 96 | % |  |  | ref 2016 | combination | combination
| E/P ratio limitation | 0.04 | 0.04 | 0.04 | h |  |  | 9 | 9 | 9
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Date |  | Type |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | https://sei.info.yorku.ca/files/2013/03/Sauer2.pdf | June 2012 |  | lithium-ion batteries
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | https://www.agora-energiewende.de/fileadmin/Projekte/2013/speicher-in-der-energiewende/Agora_Speicherstudie_Web.pdf | September 2014 |  | lithium-ion batteries
| 3 | Batteriespeicher in der Nieder- und Mittelspannungsebene | VDE | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | Mai 2015 |  | lithium-ion batteries
| 4 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.acatech.de/fileadmin/user_upload/Baumstruktur_nach_Website/Acatech/root/de/Publikationen/Materialien/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015 |  | lithium-ion batteries
| 5 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | Titanate
| 6 | The Technical Advantages of Lithium Titanate (LTO) Cells for Enhanced Energy Efficiency |  | https://www.global-batteries.com/the-technical-advantages-of-lithium-titanate-lto-cells-for-enhanced-energy-efficiency/ | April 2025 |  | Titanate
| 7 | What are the advantages of lithium titanate batteries? |  | https://www.youth-battery.com/what-are-the-advantages-of-lithium-titanate-batteries | April 2025 |  | Titanate
| 8 | Lithium-titanate batteries: Everything you need to know | Ana Lejtman | https://climatebiz.com/lithium-titanate-batteries | December 2022 |  | Titanate
| 9 | State-of-charge estimator design and experimental verification for a lithium-titanate battery cell | Pavkovic, Danijel | https://link.springer.com/article/10.1007/s10098-024-02894-z | May 2024 |  | Titanate
| 10 | BNEF energy storage outlook 2023 | BNEF | https://about.bnef.com/ | 2023 |  | LFP | Used as a reference to seperate cell from system costs (see calculation in supporting documentation)
Percental
Interpolation
Source 1 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2
| Energy installation cost | 1050 | 726.429 |  | 458.3509 | 289.2031 |  | USD / kWh | 0.087987
| Power installation cost | 0 | 0 |  | 0 | 64.2674 |  | USD / kW | 0
| Cycle life | 10000 | 8841.9219 |  | 7581.0614 | 6500 |  | equivalent full-cycles | 0.030302
| Calendar life | 15 | 16.285 |  | 18.0472 | 20 |  | a | -0.020761
| Round-trip efficiency | 96 | 93.9456 |  | 91.4394 | 89 |  | % | 0.0053934
Source 2 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 1050 | 659.1002 | 464.8074 | 442.9207 | 392.6073 | 365.2058 | USD / kWh | 0.1099 | 0.023828
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 10000 | [5 empty] | equivalent full-cycles
| Calendar life | 15 | 15 | 15 | 15.8884 | 18.3463 | 20 | a | 0 | -0.029186
| Round-trip efficiency | 96 | 92.5241 | 90 | 90 | 90 | 90 | % | 0.0091774 | 0
Source 3 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 1050 | 199.778 |  | 160.9323 | 129.6399 |  | USD / kWh | 0.13879 | 0.042323
| Power installation cost | 0 | [5 empty] | USD / kW | #DIV/0!
| Cycle life | 10000 | 6500 |  | 6500 | 6500 |  | equivalent full-cycles | 0.030302 | 0
| Calendar life | 15 | 20 |  | 20 | 20 |  | a | -0.020761 | 0
| Round-trip efficiency | 96 | 87.5 |  | 87.5 | 87.5 |  | % | 0.0066002 | 0
Source 4 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 1050 | 677.0904 | 487.2364 | 473.0983 | 439.5219 | 327.414 | USD / kWh | 0.10388 | 0.014615
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 10000 | 10920.8215 | 11666.6667 | 12141.8898 | 13416.37 | 20000 | equivalent full-cycles | -0.022266 | -0.020163
| Calendar life | 15 | 16.1121 | 17 | 17.4398 | 18.5899 | 24 | a | -0.018041 | -0.012854
| Round-trip efficiency | 96 | 90.7489 | 87 | 87.2188 | 87.768 | 90 | % | 0.013964 | -0.0012564
Source 5 |  | 2016 | 2017 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 1050 | 650 | 600 | 525.0666 | 459.4916 |  | USD / kWh | 0.38095 | 0.026328
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 10000 | [5 empty] | equivalent full-cycles
| Calendar life | 15 | [5 empty] | a
| Round-trip efficiency | 96 | [5 empty] | %
Source 6 |  | 2016 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 1050 | 400 | 233.997 | USD / kWh | 0.10168
| Power installation cost | 0 |  |  | USD / kW
| Cycle life | 10000 | 25000 | 41592.7649 | equivalent full-cycles | -0.10717
| Calendar life | 15 | 25 | 33.2039 | a | -0.0584
| Round-trip efficiency | 96 |  |  | %
Source 7 |  | 2016 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 1050 | 550 | 384.0148 | USD / kWh | 0.069327
| Power installation cost | 0 |  |  | USD / kW
| Cycle life | 10000 | 17500 | 23881.3672 | equivalent full-cycles | -0.064153
| Calendar life | 15 |  |  | a
| Round-trip efficiency | 96 |  |  | %
Source 8 |  | 2016 | 2022 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 1050 |  |  |  | USD / kWh
| Power installation cost | 0 |  |  |  | USD / kW
| Cycle life | 10000 | 6400 | 6400 | 6400 | equivalent full-cycles
| Calendar life | 15 |  |  |  | a
| Round-trip efficiency | 96 |  |  |  | %
Source 9 |  | 2016 | 2022 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 1050 |  | 422 | 254.3202 | USD / kWh | 0.096322
| Power installation cost | 0 |  |  |  | USD / kW
| Cycle life | 10000 |  |  |  | equivalent full-cycles
| Calendar life | 15 |  |  |  | a
| Round-trip efficiency | 96 |  |  |  | %
| E/P ratio limitation |  |  | 0.04 |  | h
Source 9+10 |  | 2016 | 2022 | 2025 | 2030 | unit | X1 | X2
| Energy installation cost | 1050 |  | 422 | 254.3202 | USD / kWh | 0.096322
| Power installation cost | 0 |  |  |  | USD / kW
| Cycle life | 10000 |  |  |  | equivalent full-cycles
| Calendar life | 15 |  |  |  | a
| Round-trip efficiency | 96 |  |  |  | %

## Li-Ion (Titanate) (hidden)
| 2016 |  |  | 2025 |  |  | 2030
Li-Ion (Titanate) (calc) | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 620 | 200 | 350 | 620 | 200 | 350 | 620 | 200 | 350 | Wh/l
Power density | 10000 | 100 | 3500 | 10000 | 100 | 3500 | 10000 | 100 | 3500 | W/l
Cycle life | 20000 | 5000 | 10000 | 35000 | 8750 | 17500 | 48000 | 12000 | 24000 | equivalent full-cycles
Calendar life | 20 | 10 | 15 | 22.6667 | 11.3333 | 17 | 26.6667 | 13.3333 | 20 | a
Depth of discharge | 100 | 84 | 95 | 100 | 84 | 95 | 100 | 84 | 95 | %
Round-trip efficiency | 98 | 80 | 96 | 98 | 80 | 96 | 98 | 80 | 96 | %
Self-discharge | 0.09 | 0.36 | 0.05 | 0.09 | 0.36 | 0.05 | 0.09 | 0.36 | 0.05 | % per day
Power dynamic | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 472.5 | 1260 | 1050 | 189.9 | 506.4 | 422 | 114.3 | 304.8 | 254 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 50 | USD / kW
E/P ratio limitation | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | h

## SIB (Layered oxide) (calc) (hidden)
| SIB (Layered oxide) | [7 empty] | Sources
|  | 2025 - low | 2025 - high | 2030 | unit |  | Source 2025 (low) | Source 2025 (high) | Source 2030
| Energy installation cost | 236 | 269 | 213 | USD / kWh |  | combination | combination | 1
| Power installation cost | 0 | 0 | 0 | USD / kW |  | 1 | 1 | 1
| Cycle life | 1500 | 1500 | 1500 | equivalent full-cycles |  | combination | combination | combination
| Calendar life | 15 | 20 | 17.5 | a |  | combination | combination | combination
| Energy density | 200 | 300 | 375 |  |  | 6 | 6 | assumption based on 6
| Round-trip efficiency | 90 | 93 | 93 | % |  | combination | combination | combination
| E/P ratio limitation | 0.25 | 0.25 | 0.25 | h |  | 6 | 6 | 6
interpolated
| References | [7 empty] | extrapolated
| Number of Source | Titel | Authors | Web |  | Type |  |  | not needed or not available
| 1 | Critically assessing sodium-ion technology roadmaps and scenarios for techno-economic competitiveness against lithium-ion batteries | Yao, Benson, Chueh | https://www.nature.com/articles/s41560-024-01701-9.pdf | June 2024 | sodium-ion batteries
| 2 | Techno-economics Analysis on Sodium-Ion Batteries: Overview and Prospective | Marco Ferraro, Giovanni Tumminia | https://link.springer.com/chapter/10.1007/978-3-031-48359-2_14 | February 2024 | sodium-ion batteries
| 3 | Improvement of cycle life for layered oxide cathodes in sodium-ion batteries | Huan Yang, Dong Wang, Yalan Liu, Yihua Liu, Benhe Zhong, Yang Song, Qingquan Kong, Zhenguo Wu, Xiaodong Guo | https://pubs.rsc.org/en/content/articlelanding/2024/ee/d3ee02934d | 2024 | sodium-ion batteries
| 4 | High-Energy, High-Power Sodium-Ion Batteries from a Layered Organic Cathode | Tianyang Chen, Jiande Wang, Bowen Tan, Kimberly J. Zhang, Harish Banda, Yugang Zhang, Dong-Ha Kim, Mircea Dincă | https://pubs.acs.org/doi/10.1021/jacs.4c17713 | February 2025 | sodium-ion batteries
| 5 | 2021 roadmap for sodium-ion batteries | Nuria Tapia-Ruiz, A Robert Armstrong, Hande Alptekin, Marco A Amores, Heather Au, Jerry Barker, Rebecca Boston, William R Brant, Jake M Brittain, Yue Chen, Manish Chhowalla, Yong-Seok Choi, Sara I R Costa, Maria Crespo Ribadeneyra, Serena A Cussen, Edmund J Cussen, William I F David, Aamod V Desai, Stewart A M Dickson, Emmanuel I Eweka, Juan D Forero-Saboya, Clare P Grey, John M Griffin, Peter Gross, Xiao Hua, John T S Irvine, Patrik Johansson, Martin O Jones, Martin Karlsmo, Emma Kendrick, Eunjeong Kim, Oleg V Kolosov, Zhuangnan Li, Stijn F L Mertens, Ronnie Mogensen, Laure Monconduit, Russell E Morris, Andrew J Naylor, Shahin Nikman, Christopher A O’Keefe, Darren M C Ould, R G Palgrave, Philippe Poizot, Alexandre Ponrouch, Stéven Renault, Emily M Reynolds, Ashish Rudola, Ruth Sayers, David O Scanlon, S Sen, Valerie R Seymour, Begoña Silván, Moulay Tahar Sougrati, Lorenzo Stievano, Grant S Stone, Chris I Thomas, Maria-Magdalena Titirici, Jincheng Tong, Thomas J Wood, Dominic S Wright and Reza Younesi | https://iopscience.iop.org/article/10.1088/2515-7655/ac01ef | July 2021 | sodium-ion batteries
| 6 | Alternative Battery Technologies Roadmap 2030+ | Fraunhofer ISI | https://www.isi.fraunhofer.de/content/dam/isi/dokumente/cct/2023/abt-roadmap.pdf | September 2023 | sodium-ion batteries
Percental
Interpolation
Source 1 |  | 2025 | 2030 | unit | X2
| Energy installation cost | 269 | 232 | USD / kWh
| Power installation cost |  |  | USD / kW
| Cycle life |  |  | equivalent full-cycles
| Calendar life |  |  | a
| Round-trip efficiency |  |  | %
Source 2 |  | 2024
| Energy installation cost | 241.342
Power installation cost
Cycle life
Calendar life
Round-trip efficiency
Source 3 |  | 2023
Energy installation cost
Power installation cost
| Cycle life | 1500
Calendar life
Round-trip efficiency
Source 4 |  | 2025
Energy installation cost
Power installation cost
Cycle life
Calendar life
| Round-trip efficiency | 90
Source 5 |  | 2021
Energy installation cost
Power installation cost
Cycle life
Calendar life
| Round-trip efficiency | 93
Source 6 |  | 2021 | 2025 | 2030 | 2050 | unit | X1 | X2
| Energy density | 200-300 |  |  | >300 | Wh/l
| Energy installation cost | 256.2162 | 236.0074 | 212.973 |  | USD / kWh | 0.02033
| Power installation cost |  |  |  |  | USD / kW
| Cycle life | 1000 | 1210.7173 | 1537.61 | 4000 | equivalent full-cycles | -0.048964
| Calendar life | 15 |  |  | >15 | a
| Round-trip efficiency | >90 |  |  | >95 | %
| E/P ratio limitation | >0.25 |  |  |  | h

## SIB (Layered oxide) (hidden)
| 2016 |  |  | 2025 |  |  | 2030
SIB (Layered oxide) (calc) | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | #N/A | #N/A | #N/A | 300 | 200 | 250 | 450 | 300 | 375 | Wh/l
Power density | #N/A | #N/A | #N/A | 1200 | 800 | 1000 | 1800 | 1200 | 1500 | W/l
Cycle life | #N/A | #N/A | #N/A | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | equivalent full-cycles
Calendar life | #N/A | #N/A | #N/A | 20 | 15 | 17.5 | 20 | 15 | 17.5 | a
Depth of discharge | #N/A | #N/A | #N/A | 100 | 84 | 90 | 100 | 84 | 90 | %
Round-trip efficiency | #N/A | #N/A | #N/A | 93 | 90 | 91.5 | 93 | 90 | 91.5 | %
Self-discharge | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | % per day
Power dynamic | #N/A | #N/A | #N/A | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | s to rated power
Planning & Construction Time | #N/A | #N/A | #N/A | 0 | 0 | - | 0 | 0 | - | a
Energy installation cost | #N/A | #N/A | #N/A | 269 | 236 | 252.5 | 226.9188 | 199.0812 | 213 | USD / kWh
Power installation cost | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
E/P ratio limitation | #N/A | #N/A | #N/A | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | h

## ZnBr (Zinc ion) (calc) (hidden)
| ZnBr (Zinc ion) | [8 empty] | Sources
|  | 2025 (low) | 2025 ( high) | 2030 | unit |  |  | Source 2025 (low) | Source 2025 (high) | Source 2030
| Energy installation cost | 205 | 353 | 153 | USD / kWh |  |  | 1 | 1 | 1
| Power installation cost | 0 | 0 | 0 | USD / kW
| Cycle life | 856 | 10000 | 5428 | equivalent full-cycles |  |  | combination | combination | combination
| Calendar life | 10 | 20 | 20 | a |  |  | 4 | 4 | 4
| Depth of discharge | 5 | 50 | 50 |  |  |  | 8 | 7 | same as 2025 high
| Energy density | 40 | 100 | 140 | Wh/l |  |  | 5 | 5 | average from range in 5
| Round-trip efficiency | 70 | 80 | 90 | % |  |  | 8 | 7 | 5
| E/P ratio limitation (best) | 0.8 | 0.8 | 0.6 | h |  |  | 5 | 5 | 5
| E/P ratio limitation (worst) | 16.5 | 16.5 | 13 | h |  |  | 5 | 5 | 5
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Date |  | Type |  |  | not needed or not available
| 1 | 137 Year Old Battery Tech May Be The Future of Energy Storage | Matt Ferrell, Sunny Natividad | https://undecidedmf.com/137-year-old-battery-tech-may-be-the-future-of-energy-storage | December 2022 |  | zinc-ion
| 2 | Charge less, power more: Zinc-bromine battery tech hits record 10,000 charge cycles | Sujita Sinha | https://interestingengineering.com/energy/novel-electrode-for-improving-flowless-zinc-bromine-battery | July 2024 |  | zinc-ion
| 3 | New zinc-ion battery with longer lifespan | Tage Erikson | https://www.bestmag.co.uk/new-zinc-ion-battery-with-longer-lifespan/ | June 2025 |  | zinc-ion
| 4 | Eos Z3 |  | https://www.eose.com/wp-content/uploads/2023/05/eos_productsheet_Z3_050223.pdf | May 2023 |  | zinc-ion
| 5 | Alternative Battery Technologies Roadmap 2030+ | Fraunhofer ISI | https://www.isi.fraunhofer.de/content/dam/isi/dokumente/cct/2023/abt-roadmap.pdf | September 2023 |  | zinc-ion
| 6 | Energy Storage Grand Challenge Cost and Performance Assessment 2022 | PNNL | https://www.pnnl.gov/sites/default/files/media/file/ESGC%20Cost%20Performance%20Report%202022%20PNNL-33283.pdf | August 2022 |  | zinc-ion
| 7 | Open challenges and good experimental practices in the research field of aqueous Zn-ion batteries | La Mantia | nature.com/articles/s41467-022-28381-x.pdf?utm_source=scopus&getft_integrator=scopus#page=1.88 | 2022 |  | zinc-ion
| 8 | Reassessing the Commercialization of Aqueous Zinc-Ion Batteries Based on Laboratory Achievements | Jian et al. | Reassessing the Commercialization of Aqueous Zinc-Ion Batteries Based on Laboratory Achievements ¦ ACS Applied Energy Materials | 2025 |  | zinc-ion
| 9 | Zinc-ion batteries for stationary energy storage | Gourley et al. | Zinc-ion batteries for stationary energy storage - ScienceDirect | 2023 |  | zinc-ion
Percental
Interpolation
Source 1 |  | 2022
| Energy installation cost | 153
Power installation cost
Cycle life
Calendar life
| Round-trip efficiency | 87
Source 2 |  | 2024
Energy installation cost
Power installation cost
| Cycle life | 10000
Calendar life
Round-trip efficiency
Source 3 |  | 2025
Energy installation cost
Power installation cost
| Cycle life | 5000
Calendar life
Round-trip efficiency
Source 4 |  | 2023
Energy installation cost
Power installation cost
| Cycle life | 6000
| Calendar life | 20
| Round-trip efficiency | 85
Source 5 |  | 2021 | 2025 | 2030 | 2050 | unit | X1 | X2
| Energy Density | 40-100 |  |  | 80-200 | Wh/l
| Energy installation cost | 369.7297 | 352.9301 | 333 |  | USD / kWh | 0.011558
| Power installation cost |  |  |  |  | USD / kW
| Cycle life | 700 | 855.6057 | 1099.6214 | 3000 | equivalent full-cycles | -0.051463
| Calendar life |  |  |  |  | a
| Round-trip efficiency | >80 |  |  | 90 | %
| E/P ratio limitation (worst) | 20 | 16.5191 | 13.0072 | 5 | h | 0.046679
| E/P ratio limitation (best) | 1 | 0.80092 | 0.60685 | 0.2 | h | 0.053986
Source 6 |  | 2021 | 2025 | 2030 | 2050 | unit | X1 | X2
| Energy installation cost | 315 | 205.1308 | 120 |  | USD / kWh | 0.10168
| Power installation cost |  |  |  |  | USD / kW
| Cycle life |  |  |  |  | equivalent full-cycles
| Calendar life |  |  |  |  | a
| Round-trip efficiency |  |  |  |  | %
Source 7 |  | 2021 | 2025 | 2030 | 2050 | unit | X1 | X2
| Depth of discharge |  | <100 |  |  | Wh/l
| Cycle life |  | 1000 | 3000 |  | equivalent full-cycles
| Round-trip efficiency |  | 80 |  |  | %
Source 8 |  | 2021 | 2025 | 2030 | 2050 | unit | X1 | X2
| Energy Density |  | 35-60 |  |  | Wh/l
| Cycle life |  | 1000 | 6500 |  | equivalent full-cycles
| Round-trip efficiency |  | 70 |  |  | %
Source 9 |  | 2021 | 2025 | 2030 | 2050 | unit | X1 | X2
| Energy density |  | 100 | 450 |  | Wh/l

## ZnBr (Zinc ion) (hidden)
| 2016 |  |  | 2025 |  |  | 2030
ZnBr (Zinc ion) (calc) | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | #N/A | #N/A | #N/A | 100 | 40 | 70 | 200 | 80 | 140 | Wh/l
Power density | #N/A | #N/A | #N/A | 125 | 50 | 87.5 | 333.3333 | 133.3333 | 233.3333 | W/l
Cycle life | #N/A | #N/A | #N/A | 10000 | 856 | 5428 | 10000 | 856 | 5428 | equivalent full-cycles
Calendar life | #N/A | #N/A | #N/A | 20 | 10 | 15 | 26.6667 | 13.3333 | 20 | a
Depth of discharge | #N/A | #N/A | #N/A | 100 | 84 | 95 | 100 | 84 | 95 | %
Round-trip efficiency | #N/A | #N/A | #N/A | 80 | 70 | 75 | 96 | 84 | 90 | %
Self-discharge | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | % per day
Power dynamic | #N/A | #N/A | #N/A | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | s to rated power
Planning & Construction Time | #N/A | #N/A | #N/A | 0 | 0 | - | 0 | 0 | - | a
Energy installation cost | #N/A | #N/A | #N/A | 205 | 353 | 279 | 112.4194 | 193.5806 | 153 | USD / kWh
Power installation cost | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
E/P ratio limitation | #N/A | #N/A | #N/A | 0.8 | 16.5 | 8.65 | 0.6 | 13 | 6.8 | 1/h

## NaNiCl (calc) (hidden)
| NaNiCl | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030
| Energy installation cost | 399 | 354 | 306 | 264 | USD / kWh |  | ref 2016 | 3 | 3 | 3
| Power installation cost | 0 |  |  |  | USD / kW |  | ref 2016
| Cycle life | 3000 |  |  |  | equivalent full-cycles |  | ref 2016
| Calendar life | 15 |  |  |  | a |  | ref 2016
| Round-trip efficiency | 84 |  |  |  | % |  | ref 2016
| E/P ratio limitation | 6 | 6 | 6 | 6 | h |  | 3 | 3 | 3 | 3
Note: As no reliable data could be found, a simple estimation of 3% annual performance increase / price decrease was used as a reference. For the round-trip efficiency, an increase of 1 percent point per period was assumed.
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Data |  | Type |  |  | not needed or not available
| 1 | Agora Stromspeicher in der Energiewende | Agora Energiewende | https://www.agora-energiewende.de/fileadmin/Projekte/2013/speicher-in-der-energiewende/Agora_Speicherstudie_Web.pdf | September 2014 |  | NaS/NaCl
| 2 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | sodium metal halide
| 3 | Alternative Battery Technologies Roadmap 2030+ | Fraunhofer ISI | https://www.isi.fraunhofer.de/content/dam/isi/dokumente/cct/2023/abt-roadmap.pdf | September 2023 |  | NaS/NaCl
Percental
Interpolation
Source 1 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2
| Energy installation cost | 399 | 310.5678 | 332.0053 | 227.0574 | 166.0027 |  | USD / kWh | 0.060718
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 3000 | [5 empty] | equivalent full-cycles
| Calendar life | 15 | [5 empty] | a
| Round-trip efficiency | 84 | [5 empty] | %
Source 2 |  | 2016 | 2017 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 399 | 465 | 400 | 311.223 | 242.1494 |  | USD / kWh | -0.16541 | 0.048952
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 3000 | [5 empty] | equivalent full-cycles
| Calendar life | 15 | [5 empty] | a
| Round-trip efficiency | 84 | [5 empty] | %
Source 3 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 399 | 354.4444 | 324.3243 | 305.6801 | 263.6247 |  | USD / kWh | 0.029169
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 3000 | [5 empty] | equivalent full-cycles
| Calendar life | 15 | [5 empty] | a
| Round-trip efficiency | 84 | [5 empty] | %
| E/P ratio limitation |  |  | 6 |  |  |  | h

## NaNiCl (hidden)
| 2016 |  |  | 2025 |  |  | 2030
NaNiCl (calc) | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 280 | 150 | 215 | 280 | 150 | 215 | 280 | 150 | 215 | Wh/l
Power density | 270 | 150 | 210 | 270 | 150 | 210 | 270 | 150 | 210 | W/l
Cycle life | 7500 | 1000 | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
Calendar life | 22 | 8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | a
Depth of discharge | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Round-trip efficiency | 92 | 80 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | %
Self-discharge | 0.05 | 15 | 5 | 0.05 | 15 | 5 | 0.05 | 15 | 5 | % per day
Power dynamic | 0.1 | < 1 | 0.5 | 0.1 | 0 | 0.5 | 0.1 | 0 | 0.5 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 315 | 488 | 399 | 241.5789 | 374.2556 | 306 | 208.4211 | 322.8872 | 264 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
E/P ratio limitation | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | h

## NaS (calc) (hidden)
| NaS | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030
| Energy installation cost | 525 | 395.9438 | 283.4745 | 200 | USD / kWh |  | ref 2016 | combination | combination | 5
| Power installation cost | 0 | 122 | 78 | 50 | USD / kW |  | ref 2016 | 1 | 1 | 1
| Cycle life | 5000 | 5500 | 6500 | 7500 | equivalent full-cycles |  | ref 2016 | combination | combination | combination
| Calendar life | 17 | 19 | 22 | 25 | a |  | ref 2016 | combination | combination | combination
| Round-trip efficiency | 80 | 81 | 83 | 85 | % |  | ref 2016 | combination | combination | combination
| E/P ratio limitation | 6 | 6 | 6 | 6 | h |  | 5 | 5 | 5 | 5
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Data |  | Type |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | https://sei.info.yorku.ca/files/2013/03/Sauer2.pdf | June 2012 |  | High temperature batteries (NaS)
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | https://www.agora-energiewende.de/fileadmin/Projekte/2013/speicher-in-der-energiewende/Agora_Speicherstudie_Web.pdf | September 2014 |  | NaS/NaCl
| 3 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | November 2015 |  | sodium sulphur batteries
| 4 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | sodium sulphur
| 5 | Alternative Battery Technologies Roadmap 2030+ | Fraunhofer ISI | https://www.isi.fraunhofer.de/content/dam/isi/dokumente/cct/2023/abt-roadmap.pdf | September 2023 |  | NaS/NaCl
Percental
Interpolation
Source 1 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2
| Energy installation cost | 525 | 365.5026 |  | 232.4365 | 147.8149 |  | USD / kWh | 0.086554
| Power installation cost | 0 | 0 |  | 0 | 64.2674 |  | USD / kW | 0
| Cycle life | 5000 | 5614.1213 |  | 6488.9067 | 7500 |  | equivalent full-cycles | -0.029385
| Calendar life | 17 | 18.9803 |  | 21.7832 | 25 |  | a | -0.02793
| Round-trip efficiency | 80 | 81.3978 |  | 83.1794 | 85 |  | % | -0.0043397
Source 2 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 525 | 404.0516 | 332.0053 | 289.0274 | 204.3732 | 166.0027 | USD / kWh | 0.063367 | 0.066967
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 5000 | [5 empty] | equivalent full-cycles
| Calendar life | 17 | [5 empty] | a | 1
| Round-trip efficiency | 80 | 77.1034 | 75 | 75 | 75 | 75 | % | 0.0091774 | 0
Source 3 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 525 | 276.4814 | 170.9212 | 166.6011 | 156.2725 | 120.9767 | USD / kWh | 0.14812 | 0.012719
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 5000 | 6059.9876 | 7000 | 7285.1339 | 8049.822 | 12000 | equivalent full-cycles | -0.049241 | -0.020163
| Calendar life | 17 | 22.1441 | 27 | 27.3419 | 28.2159 | 32 | a | -0.068322 | -0.0063124
| Round-trip efficiency | 80 | 83.3754 | 86 | 86.0737 | 86.2582 | 87 | % | -0.010385 | -0.00042827
Source 4 |  | 2016 | 2017 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 525 | 535 | 500 | 446.6805 | 399.047 |  | USD / kWh | -0.019048 | 0.0223
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 5000 | [5 empty] | equivalent full-cycles
| Calendar life | 17 | [5 empty] | a
| Round-trip efficiency | 80 | [5 empty] | %
Source 5 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 525 | 398.6833 | 324.3243 | 282.6271 | 200.3548 |  | USD / kWh | 0.066494
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 5000 |  | 4500 |  | >7000 |  | equivalent full-cycles
| Calendar life | 17 |  | >15 |  | 20 |  | a
| Round-trip efficiency | 80 |  | 70-80 |  | >80 |  | %
| E/P ratio limitation |  |  | 6 |  |  |  | h

## NaS (hidden)
| 2016 |  |  | 2025 |  |  | 2030
NaS (calc) | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 300 | 140 | 250 | 300 | 140 | 250 | 300 | 140 | 250 | Wh/l
Power density | 160 | 120 | 140 | 160 | 120 | 140 | 160 | 120 | 140 | W/l
Cycle life | 10000 | 1000 | 5000 | 13000 | 1300 | 6500 | 15000 | 1500 | 7500 | equivalent full-cycles
Calendar life | 25 | 10 | 17 | 32.3529 | 12.9412 | 22 | 36.7647 | 14.7059 | 25 | a
Depth of discharge | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Round-trip efficiency | 90 | 70 | 80 | 93.375 | 72.625 | 83 | 95.625 | 74.375 | 85 | %
Self-discharge | 0.05 | 20 | 7 | 0.05 | 20 | 7 | 0.05 | 20 | 7 | % per day
Power dynamic | 3 | 20 | 10 | 3 | 20 | 10 | 3 | 20 | 10 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 367.5 | 735 | 525 | 198.4322 | 396.8644 | 283.4745 | 140 | 280 | 200 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 50 | USD / kW
E/P ratio limitation | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | h

## Vanadium Flow (calc) (hidden)
| Vanadium Flow | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030
| Energy installation cost | 346.5 | 440.9324 | 401.5696 | 335.9106 | USD / kWh |  | ref 2016 | combination | combination | combination
| Power installation cost | 1312.5 | 1224 | 1122 | 1028 | USD / kW |  | ref 2016 | 1 | 1 | 1
| Cycle life | 13000 | 13000 | 13000 | 13000 | equivalent full-cycles |  | ref 2016 | combination | combination | combination
| Calendar life | 12 | 14 | 16 | 20 | a |  | ref 2016 | combination | combination | 5
| Round-trip efficiency | 70 | 70 | 71 | 72 | % |  | ref 2016 | combination | combination | combination
| Depth of discharge (worst) | 15 | 80 | 80 | 80 | % |  | ref 2016 | combination | combination | combination
| Max. C-rate (best) | 5 | 5 | 5 | 5 | h |  | 5 | 5 | 5 | 5
| Max. C-rate (worst) | 10 | 10 | 10 | 10 | h |  | 5 | 5 | 5 | 5
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Data |  | Type |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | https://sei.info.yorku.ca/files/2013/03/Sauer2.pdf | June 2012 |  | flow batteries
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | https://www.agora-energiewende.de/fileadmin/Projekte/2013/speicher-in-der-energiewende/Agora_Speicherstudie_Web.pdf | September 2014 |  | redox flow batteries
| 3 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | November 2015 |  | redox flow batteries
| 4 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | flow batteries
| 5 | Alternative Battery Technologies Roadmap 2030+ | Fraunhofer ISI | https://www.isi.fraunhofer.de/content/dam/isi/dokumente/cct/2023/abt-roadmap.pdf | September 2023 |  | vanadium flow
| 6 | Energy Storage Grand Challenge Cost and Performance Assessment 2022 | PNNL | https://www.pnnl.gov/sites/default/files/media/file/ESGC%20Cost%20Performance%20Report%202022%20PNNL-33283.pdf | August 2022 |  | vanadium flow
| 7 | Techno-economic analysis of Aqueous Organic Redox Flow Batteries: Stochastic investigation of capital cost and levelized cost of storage | Cremoncini, Diana et al. | https://www.sciencedirect.com/science/article/pii/S0306261924001211/pdfft?md5=a80ff369138f4b0030c3945fb040e611&pid=1-s2.0-S0306261924001211-main.pdf | April 2024 |  | vanadium flow
Percental
Interpolation
Source 1 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2
| Energy installation cost | 346.5 | 268.2116 |  | 194.7356 | 141.3882 |  | USD / kWh | 0.06202
| Power installation cost | 1312.5 | 1224.0996 |  | 1121.9244 | 1028.2776 |  | USD / kW | 0.017281
| Cycle life | 13000 | [5 empty] | equivalent full-cycles | 1
| Calendar life | 12 | 13.8857 |  | 16.6647 | 20 |  | a | -0.037161
| Round-trip efficiency | 10 | 17.6467 |  | 35.8916 | 73 |  | % | -0.15257
Source 2 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 346.5 | 502.4764 | 664.0106 | 609.1969 | 491.1503 | 431.6069 | USD / kWh | -0.09737 | 0.042164
| Power installation cost | 1312.5 | [5 empty] | USD / kW
| Cycle life | 13000 | [5 empty] | equivalent full-cycles
| Calendar life | 12 | [5 empty] | a
| Round-trip efficiency | 10 | 29.1422 | 65 | 65 | 65 | 65 | % | -0.30656 | 0
Source 3 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 346.5 | 231.381 | 170.9212 | 166.6011 | 156.2725 | 120.9767 | USD / kWh | 0.096026 | 0.012719
| Power installation cost | 1312.5 | [5 empty] | USD / kW
| Cycle life | 13000 | 13000 | 13000 | 13000 | 13000 | 13000 | equivalent full-cycles | 0 | 0
| Calendar life | 12 | 14.6427 | 17 | 17.3278 | 18.1752 | 22 | a | -0.051017 | -0.009595
| Round-trip efficiency | 10 | 30.4028 | 70 | 70.2887 | 71.0158 | 74 | % | -0.32047 | -0.0020603
Source 4 |  | 2016 | 2017 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 346.5 | 550 | 350 | 164.7822 | 77.5805 |  | USD / kWh | -0.5873 | 0.13986
| Power installation cost | 1312.5 | [5 empty] | USD / kW
| Cycle life | 13000 | [5 empty] | equivalent full-cycles
| Calendar life | 12 | [5 empty] | a
| Round-trip efficiency | 10 | [5 empty] | %
Source 5 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2035 | unit
| Energy installation cost | 346.5 |  | 464.8649 | 421.8103 | 330.8212 | 259.4595 | USD / kWh | 0.047434
| Power installation cost | 1312.5 | [5 empty] | USD / kW
| Cycle life | 13000 |  | >10000 |  |  |  | equivalent full-cycles
| Calendar life | 12 |  | 20 |  |  | 20 | a
| Round-trip efficiency | 70 |  | 60-90 |  |  |  | %
| E/P ratio limitation |  |  | 5 - 10 |  |  |  | h
Source 6 |  | 2016 | 2020 | 2021 | 2025 | 2030 | 2035 | unit
| Energy installation cost | 346.5 |  | 417 | 381.3289 | 341 |  | USD / kWh | 0.022108
| Power installation cost | 1312.5 | [5 empty] | USD / kW
| Cycle life | 13000 |  | Unlimited |  | Unlimited |  | equivalent full-cycles
| Calendar life | 12 |  | 12 |  | 12 |  | a
| Round-trip efficiency | 70 |  | 65 |  | 65 |  | %
| Depth of discharge | 10 |  | 80 |  | 80 |  | %
Source 7 |  | 2016 | 2020 | 2024 | 2025 | 2030 | 2035 | unit
| Energy installation cost | 346.5 |  | 474.026 |  |  |  | USD / kWh | 1
| Power installation cost | 1312.5 | [5 empty] | USD / kW
| Cycle life | 13000 | [5 empty] | equivalent full-cycles
| Calendar life | 12 | [5 empty] | a
| Round-trip efficiency | 70 | [5 empty] | %

## Vanadium Flow (hidden)
| 2016 |  |  | 2025 |  |  | 2030
Vanadium Flow (calc) | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 70 | 15 | 45 | 70 | 15 | 45 | 70 | 15 | 45 | Wh/l
Power density | 2 | 0.5 | 1.3 | 2 | 0.5 | 1.3 | 2 | 0.5 | 1.3 | W/l
Cycle life | 14000 | 12000 | 13000 | 14000 | 12000 | 13000 | 14000 | 12000 | 13000 | equivalent full-cycles
Calendar life | 20 | 5 | 12 | 26.6667 | 6.6667 | 16 | 33.3333 | 8.3333 | 20 | a
Depth of discharge | 100 | 10 | 55 | 100 | 10 | 55 | 100 | 10 | 55 | %
Round-trip efficiency | 85 | 60 | 70 | 86.2143 | 60.8571 | 71 | 87.4286 | 61.7143 | 72 | %
Self-discharge | 0 | 1 | 0.15 | 0 | 1 | 0.15 | 0 | 1 | 0.15 | % per day
Power dynamic | < 0.001 | 0.02 | 0.01 | 0 | 0.02 | 0.01 | 0 | 0.02 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 315 | 1050 | 346.5 | 365.0633 | 1216.8776 | 401.5696 | 305.3733 | 1017.9109 | 335.9106 | USD / kWh
Power installation cost | 1050 | 1575 | 1312.5 | 897.6 | 1346.4 | 1122 | 822.4 | 1233.6 | 1028 | USD / kW
E/P ratio limitation | 5 | 10 | 7.5 | 5 | 10 | 7.5 | 5 | 10 | 7.5 | h

## ZnBr Flow (calc) (hidden)
| Zn/Br Flow | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030
| Energy installation cost | 900 | 653 | 547 | 484 | USD / kWh |  | ref 2016 | 5 | 5 | 5
| Power installation cost | 0 | 0 | 0 | 0 | USD / kW |  | ref 2016 | 1 | 1 | 1
| Cycle life | 10000 | 4500 | 4500 | 5000 | equivalent full-cycles |  | ref 2016 | combination | combination | combination
| Calendar life | 10 | 12 | 16 | 19 | a |  | ref 2016 | combination | combination | combination
| Round-trip efficiency | 70 | 70 | 71 | 72 | % |  | ref 2016 | combination | combination | combination
| Depth of discharge | 100 | 80 | 80 | 80 | % |  | ref 2016 | 5 | 5 | 5
| Max. C-rate (best) | 5 | 5 | 5 | 5 | h |  | 5 | 5 | 5 | 5
| Max. C-rate (worst) | 10 | 10 | 10 | 10 | h |  | 5 | 5 | 5 | 5
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Data |  | Type |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | https://sei.info.yorku.ca/files/2013/03/Sauer2.pdf | June 2012 |  | flow batteries
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | https://www.agora-energiewende.de/fileadmin/Projekte/2013/speicher-in-der-energiewende/Agora_Speicherstudie_Web.pdf | September 2014 |  | redox flow batteries
| 3 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | November 2015 |  | redox flow batteries
| 4 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | flow batteries
| 5 | Energy Storage Grand Challenge Cost and Performance Assessment 2022 | PNNL | https://www.pnnl.gov/sites/default/files/media/file/ESGC%20Cost%20Performance%20Report%202022%20PNNL-33283.pdf | August 2022 |  | vanadium flow
| 5 | Alternative Battery Technologies Roadmap 2030+ | Fraunhofer ISI | https://www.isi.fraunhofer.de/content/dam/isi/dokumente/cct/2023/abt-roadmap.pdf | September 2023 |  | vanadium flow
Percental
Interpolation
Source 1 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2
| Energy installation cost | 900 | 530.3676 |  | 273.8388 | 141.3882 |  | USD / kWh | 0.12384
| Power installation cost | 0 | 0 |  | 0 | 1028.2776 |  | USD / kW | 0
| Cycle life | 10000 | [5 empty] | equivalent full-cycles | 1
| Calendar life | 10 | 12.1901 |  | 15.6142 | 20 |  | a | -0.050757
| Round-trip efficiency | 100 | 91.4007 |  | 81.6838 | 73 |  | % | 0.022229
Source 2 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 900 | 756.4416 | 664.0106 | 609.1969 | 491.1503 | 431.6069 | USD / kWh | 0.042512 | 0.042164
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 10000 | [5 empty] | equivalent full-cycles
| Calendar life | 10 | [5 empty] | a
| Round-trip efficiency | 100 | 78.1796 | 65 | 65 | 65 | 65 | % | 0.059685 | 0
Source 3 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 900 | 348.3271 | 170.9212 | 166.6011 | 156.2725 | 120.9767 | USD / kWh | 0.21126 | 0.012719
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 10000 | 11617.4413 | 13000 | 13000 | 13000 | 13000 | equivalent full-cycles | -0.038192 | 0
| Calendar life | 10 | 13.5421 | 17 | 17.3278 | 18.1752 | 22 | a | -0.078751 | -0.009595
| Round-trip efficiency | 100 | 81.5614 | 70 | 70.2887 | 71.0158 | 74 | % | 0.049677 | -0.0020603
Source 4 |  | 2016 | 2017 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 900 | 550 | 350 | 164.7822 | 77.5805 |  | USD / kWh | 0.38889 | 0.13986
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 10000 | [5 empty] | equivalent full-cycles
| Calendar life | 10 | [5 empty] | a
| Round-trip efficiency | 100 | [5 empty] | %
Source 5 |  | 2016 | 2020 | 2021 | 2025 | 2030 | 2035 | unit
| Energy installation cost | 900 | 653.2845 | 603 | 546.8716 | 484 |  | USD / kWh | 0.076972 | 0.02413
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 10000 |  | 4563 |  | 5019 |  | equivalent full-cycles
| Calendar life | 10 |  | 12.5 |  | 15 |  | a
| Round-trip efficiency | 100 |  | 72.5 |  | 75 |  | %
| Depth of discharge | 5 |  | 80 |  | 80 |  | %
Source 5 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2035 | unit
| Energy installation cost | 900 | [5 empty] | USD / kWh
| Power installation cost | 0 | [5 empty] | USD / kW
| Cycle life | 10000 | [5 empty] | equivalent full-cycles
| Calendar life | 10 | [5 empty] | a
| Round-trip efficiency | 70 | [5 empty] | %
| E/P ratio limitation |  |  | 5 - 10 |  |  |  | h

## ZnBr Flow (hidden)
| 2016 |  |  | 2025 |  |  | 2030
ZnBr Flow (calc) | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 70 | 20 | 45 | 70 | 20 | 45 | 70 | 20 | 45 | Wh/l
Power density | 25 | 0.5 | 10 | 25 | 0.5 | 10 | 25 | 0.5 | 10 | W/l
Cycle life | 14000 | 300 | 4500 | 14000 | 300 | 4500 | 15555.5556 | 333.3333 | 5000 | equivalent full-cycles
Calendar life | 20 | 5 | 10 | 32 | 8 | 16 | 38 | 9.5 | 19 | a
Depth of discharge | 100 | 80 | 90 | 100 | 80 | 90 | 100 | 80 | 90 | %
Round-trip efficiency | 85 | 60 | 70 | 86.2143 | 60.8571 | 71 | 87.4286 | 61.7143 | 72 | %
Self-discharge | 8 | 33.6 | 15 | 8 | 33.6 | 15 | 8 | 33.6 | 15 | % per day
Power dynamic | < 0.001 | 0.02 | 0.01 | 0 | 0.02 | 0.01 | 0 | 0.02 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 525 | 1680 | 900 | 319.0833 | 1021.0667 | 547 | 282.3333 | 903.4667 | 484 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
E/P ratio limitation | 5 | 10 | 7.5 | 5 | 10 | 7.5 | 5 | 10 | 7.5 | h

## Inverter small (calc) (hidden)
| Inverter small | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030
| Energy installation cost |  |  |  |  | USD / kWh
| Power installation cost | 155.4 | 100 | 70 | 60 | USD / kW |  | ref 2016 | combination | combination | combination
| Cycle life |  |  |  |  | equivalent full-cycles
| Calendar life | 12 | 24 | 27 | 30 | a |  | ref 2016 | 1 | 1 | 1
| Round-trip efficiency | 95 | 95 | 95 | 95 | % |  | ref 2016
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Data |  | specific size |  |  | not needed or not available
| 1 | Expert Guess ISEA |  |  | October 2014 |  | no
| 2 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | November 2015 |  | no
| 3 | Batteriespeicher in der Nieder- und Mittelspannungsebene | VDE | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | Mai 2015 |  | "stationary systems"
| 4 | ISEA estimation |  |  | 2015 |  | home storage systems
Percental
Interpolation
Source 1 |  | 2016 | 2020 | 2024 | 2025 | 2030 | 2034 | unit | X1 | X2
| Energy installation cost | [6 empty] | USD / kWh
| Power installation cost | 155.4 | 122.7409 | 96.9456 | 92.7695 | 74.4377 | 62.417 | USD / kW | 0.057276 | 0.043076
| Cycle life | [6 empty] | equivalent full-cycles
| Calendar life | 12 | 18 | 27 | 27.4626 | 29.8975 | 32 | a | -0.10668 | -0.017135
| Round-trip efficiency | [6 empty] | %
Source 2 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | [6 empty] | USD / kWh
| Power installation cost | 155.4 | 107.1077 | 81.0211 | 78.169 | 71.4702 | 49.9445 | USD / kW | 0.088845 | 0.017759
| Cycle life | [6 empty] | equivalent full-cycles
| Calendar life | [6 empty] | a
| Round-trip efficiency | [6 empty] | %
Source 3 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | [6 empty] | USD / kWh
| Power installation cost | 155.4 | 102.1088 |  | 83.2408 | 67.8594 |  | USD / kW |  | 0.040037
| Cycle life | [6 empty] | equivalent full-cycles
| Calendar life | [6 empty] | a
| Round-trip efficiency | [6 empty] | %
Source 4 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | [6 empty] | USD / kWh
| Power installation cost | 155.4 | 105.4384 |  | 76.5816 | 58.8235 |  | USD / kW
| Cycle life | [6 empty] | equivalent full-cycles
| Calendar life | [6 empty] | a
| Round-trip efficiency | [6 empty] | %

## Inverter small (hidden)
| 2016 |  |  | 2025 |  |  | 2030
Inverter small (calc) | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | Wh/l
Power density | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0.15 | W/l
Cycle life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
Calendar life | 25 | 10 | 12 | 56.25 | 22.5 | 27 | 62.5 | 25 | 30 | a
Depth of discharge | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 90 | %
Round-trip efficiency | 97 | 93 | 95 | 97 | 93 | 95 | 97 | 93 | 95 | %
Self-discharge | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0.01 | % per day
Power dynamic | - | - | 0.02 | 0 | 0 | 30 | 0 | 0 | 30 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | a
Energy installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
Power installation cost | 105 | 290 | 155.4 | 47.2973 | 130.6306 | 70 | 40.5405 | 111.9691 | 60 | USD / kW

## Inverter large (calc) (hidden)
| Inverter large | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030
| Energy installation cost |  |  |  |  | USD / kWh
| Power installation cost | 105 | 85 | 70 | 55 | USD / kW |  | ref 2016 | combination | combination | combination
| Cycle life |  |  |  |  | equivalent full-cycles
| Calendar life | 20 | 24 | 27 | 30 | a |  | ref 2016 | 1 | 1 | 1
| Round-trip efficiency | 98 | 98 | 98 | 98 | % |  | ref 2016
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Data |  | specific size |  |  | not needed or not available
| 1 | Expert Guess ISEA |  |  | October 2014 |  | no
| 2 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | November 2015 |  | no
| 3 | Batteriespeicher in der Nieder- und Mittelspannungsebene | VDE | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | Mai 2015 |  | "stationary systems"
| 4 | ISEA estimation |  |  | 2015 |  | home storage systems
Percental
Interpolation
Source 1 |  | 2016 | 2020 | 2024 | 2025 | 2030 | 2034 | unit | X1 | X2
| Energy installation cost | [6 empty] | USD / kWh
| Power installation cost | 105 | 100.8924 | 96.9456 | 92.7695 | 74.4377 | 62.417 | USD / kW | 0.0099268 | 0.043076
| Cycle life | [6 empty] | equivalent full-cycles
| Calendar life | 20 | 23.2379 | 27 | 27.4626 | 29.8975 | 32 | a | -0.038226 | -0.017135
| Round-trip efficiency | [6 empty] | %
Source 2 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | [6 empty] | USD / kWh
| Power installation cost | 105 | 90.5423 | 81.0211 | 78.169 | 71.4702 | 49.9445 | USD / kW | 0.036358 | 0.017759
| Cycle life | [6 empty] | equivalent full-cycles
| Calendar life | [6 empty] | a
| Round-trip efficiency | [6 empty] | %
Source 3 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | [6 empty] | USD / kWh
| Power installation cost | 105 | 102.1088 |  | 83.2408 | 67.8594 |  | USD / kW |  | 0.040037
| Cycle life | [6 empty] | equivalent full-cycles
| Calendar life | [6 empty] | a
| Round-trip efficiency | [6 empty] | %
Source 4 |  | 2016 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | [6 empty] | USD / kWh
| Power installation cost | 105 | 105.4384 |  | 76.5816 | 58.8235 |  | USD / kW
| Cycle life | [6 empty] | equivalent full-cycles
| Calendar life | [6 empty] | a
| Round-trip efficiency | [6 empty] | %

## Inverter large (hidden)
| 2016 |  |  | 2025 |  |  | 2030
Inverter large (calc) | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | Wh/l
Power density | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0.15 | W/l
Cycle life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
Calendar life | 25 | 19 | 20 | 33.75 | 25.65 | 27 | 37.5 | 28.5 | 30 | a
Depth of discharge | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 90 | %
Round-trip efficiency | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | %
Self-discharge | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0.01 | % per day
Power dynamic | - | - | 0.02 | 0 | 0 | 30 | 0 | 0 | 30 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | a
Energy installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
Power installation cost | 73.5 | 189 | 105 | 49 | 126 | 70 | 38.5 | 99 | 55 | USD / kW

## No Inverter (hidden)
| 2016 |  |  | 2025 |  |  | 2030
No inverter | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wh/l
Power density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | W/l
Cycle life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
Calendar life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Depth of discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | %
Round-trip efficiency | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Self-discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % per day
Power dynamic | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW

## Generator PHS (hidden)
| 2016 |  |  | 2025 |  |  | 2030
Generator PHS | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wh/l
Power density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | W/l
Cycle life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
Calendar life | 80 | 40 | 50 | 80 | 40 | 50 | 80 | 40 | 50 | a
Depth of discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | %
Round-trip efficiency | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Self-discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % per day
Power dynamic | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
Please note: Only change the Calendar life in this sheet - all other values are references and need to stay that way.

## Generator CAES (hidden)
| 2016 |  |  | 2025 |  |  | 2030
Generator CAES | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wh/l
Power density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | W/l
Cycle life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
Calendar life | 80 | 40 | 50 | 80 | 40 | 50 | 80 | 40 | 50 | a
Depth of discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | %
Round-trip efficiency | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Self-discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % per day
Power dynamic | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
Power installation cost | 400 | 1050 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
Please note: Only change the Calendar life in this sheet - all other values are references and need to stay that way.

## Generator Flywheel (hidden)
| 2016 |  |  | 2025 |  |  | 2030
Generator Flywheel | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wh/l
Power density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | W/l
Cycle life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
Calendar life | 25 | 15 | 20 | 80 | 40 | 50 | 80 | 40 | 50 | a
Depth of discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | %
Round-trip efficiency | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Self-discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % per day
Power dynamic | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
Please note: Only change the Calendar life in this sheet - all other values are references and need to stay that way.

## Modular Multilevel Converter (hidden)
| 2016 (no values available) |  |  | 2025 |  |  | 2030
Modular Multilevel Converter | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wh/l
Power density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | W/l
Cycle life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
Calendar life | 0 | 0 | 0 | 40 | 30 | 35 | 40 | 30 | 35 | a
Depth of discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | %
Round-trip efficiency | 0 | 0 | 0 | 99 | 97 | 98 | 99 | 97 | 98 | %
Self-discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % per day
Power dynamic | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
Power installation cost | 0 | 0 | 0 | 150 | 500 | 250 | 150 | 500 | 250 | USD / kW
Please note: Only change the Calendar life in this sheet - all other values are references and need to stay that way.
Inserted Values are estimations based on: | https://cdn.misoenergy.org/20240131%20PSC%20Item%2005%20Transmission%20Cost%20Estimation%20Guide%20for%20MTEP24%20-%20Redline631529.pdf
https://cdn.misoenergy.org/20230531%20PAC%20Item%2008b%20MP%20RBJ%20Presentation629028.pdf
https://stabl.com/wp-content/uploads/2021/04/2021-White-Paper-MMC-DE-2.pdf